## Profile Selection
Description of Excel Tool: This spreadsheet tool is intended to assist users who are configuring an ABB ACS380, ACS480, ACS580, ACH580, ACQ580, ACS880, or DCS880 on Ethernet IP to communicate to a Rockwell PLC when replacing a Rockwell VFD with ABB VFD
The use of 1-Port modules or 2-Port Modules are identical in configuration, thus either can be used with this configuration tool.
Using this Tool:
Follow the Steps below, filling out the Highlighted cells to help guide you through the selections of drive being used.
Then click on the tab which is defined in the "Green" Highlighted box to assist with defining the needed parameter configuration along with defining the corresponding Rockwell Logix 5000 software configuration.
Note: To assist the user of this tool, please reference the comments inserted in various cells for more information.
Follow the Steps below to Determine the correct Profile Configuration for your application:
Step 1 | What ABB VFD are you configuring for Ethernet IP Communications? | [6 empty] | ACH580 |  | What Control Mode are you utilizing with the VFD? |  |  |  | Vector
[12 empty] | 16 Bit | = Word Size
Step 3 | A 2nd reference "Torque Reference" for VFD Control/Torque feeback is required. | [7 empty] | YES
Step 2 | What Rockwell VFD are you configuring for Ethernet IP Communications? | [6 empty] | Powerflex525
Step 3 | Define the Rockwell Output and Input data used. Note: Logic Command/FreqCommand/ DriveStatus/DriveFreq are automatically mapped so no need to map here | [13 empty] | Input Data (Read) (Data Read by the PLC from the VFD) The Data Shown in the Input Data Table below is exactly the order in which it will appear in the PLC and the scaling for each input signal being communicated. |  |  | Output Data (Write) (Data Sent From PLC to the VFD)
[15 empty] | Input Word # | Input Description |  | Output Word # | Output Description
| Input Data sent to the PLC from the VFD | Input 1 | DC Bus Volts |  |  |  | Output Data sent from the PLC to the VFD | Output 1 | [6 empty] | Word 1 (16bit) | Status Word |  | Word 1 (16bit) | Control Word
|  | Input 2 | Output Current |  |  |  |  | Output 2 | [6 empty] | Word 2 (16bit) | Actual Speed |  | Word 2 (16bit) | Speed Reference
|  | Input 3 | [5 empty] | Output 3 | [6 empty] | Word 3 (16bit) | Actual Torque |  | Word 3 (16bit) | Torque Reference
|  | Input 4 | [5 empty] | Output 4 | [6 empty] | Custom In 1 (Word 4 16 bit) | DC Bus Volts |  | Custom Out 1 (Word 4 16 bit) | 0
|  | Input 5 | [5 empty] | Output 5 | [6 empty] | Custom In 2 (Word 5 16 bit) | Output Current |  | Custom Out 2 (Word 5 16 bit) | 0
|  | Input 6 | [5 empty] | Output 6 | [6 empty] | Custom In 3 (Word 6 16 bit) | 0 |  | Custom Out 3 (Word 6 16 bit) | 0
|  | Input 7 | [5 empty] | Output 7 | [6 empty] | Custom In 4 (Word 7 16 bit) | 0 |  | Custom Out 4 (Word 7 16 bit) | 0
|  | Input 8 | [5 empty] | Output 8 | [6 empty] | Custom In 5 (Word 8 16 bit) | 0 |  | Custom Out 5 (Word 8 16 bit) | 0
|  | Input 9 | [5 empty] | Output 9 | [6 empty] | Custom In 6 (Word 9 16 bit) | 0 |  | Custom Out 6 (Word 9 16 bit) | 0
|  | Input 10 | [5 empty] | Output 10 | [6 empty] | Custom In 7 (Word 10 16 bit) | 0 |  | Custom Out 7 (Word 10 16 bit) | 0
[15 empty] | Custom In 8 (Word 11 16 bit) | 0 |  | Custom Out 8 (Word 11 16 bit) | 0
[15 empty] | Custom In 9 (Word 12 16 bit) | 0 |  | Custom Out 9 (Word 12 16 bit) | 0
[15 empty] | Custom In 10 (Word 13 16 bit) | 0 |  | Custom Out 10 (Word 13 16 bit) | 0
Step 4 | Define the IP Address of the VFD = |  |  |  | 192 | 168 | 3 | 3 |  | Select the Required Subnet |  |  | 255.255.255.0
| Define the Required Gateway = |  |  |  | 0 | 0 | 0 | 0
Step 7 | Only if Step 2 = "Predefined by the VFD", then complete Step 6. Select the required VFD Control Word Profile based on the available Control Bits that are available for each Profile. **Note: ODVA Extended is default, unselect if another Profile is desired.
| ODVA AC/DC Basic Profile Control Bits Consisting of: Run Forward, Fault Reset | [9 empty] | Not Selected
| ODVA AC/DC Extended Profile Control Word Bits Consisting of: Run Fwd, Run Reverse, Fault Reset | [9 empty] | Not Selected
| ABB Drives Profile Control Word Bits Consisting of: Run Command, Various Stopping Method Bits, Ramp Controls, Fault Reset, VFD Enable, Switch between 2 references or 2 Control Locations (i.e. Hand/Auto) | [9 empty] | ABB Drives
Step 5 | Click on the Tab below labeled ABB Drives Setup: | [9 empty] | ABB Drives Setup
**Important AOI Information** ABB has Add-On Instructions available for all ABB VFDs. Add-On Instructions (also known as AOIs) allow for a simplified way of importing predefined Data Tags into the Rockwell PLC to ease the integration of ABB VFDs into the ControlLogix or CompacLogix PLCs on Ethernet IP. The AOI's can be accessed from the ABB website, please use the provided link below to access the ABB Ethernet IP Connectivity Web page where the Add-On Instructions may be downloaded as a zip file. Once downloaded, unzip and run the Install.exe utility. The files are organized under folders for every ABB VFD that supports AOIs, along with the Communication Module being utilized (Note: 1-Port and 2-Port Ethernet IP Communication Modules utilized for the ACSx80 Series of "All Compatible VFDs" are identical as it pertains to configuration and use of AOIs. When running the Install utility, if default directory structures are utilized, the files for all ACSx80 series of drives are found under the following directory: C:/ABB/Add On Instructions for RSLogix 5000
https://www.abbnow.com/abbconnectivity
[21 empty] | Inputs | Input Param | Input Scaling | Outputs | Output Param | Output Scaling | Inputs | Input Param | Input Scaling | Outputs | Output Param | Output Scaling | Inputs | Input Param | Input Scaling | Outputs | Output Param | Output Scaling | Inputs | Input Param | Input Scaling16 | Input Scaling32 | Outputs | Output Param | Output Scaling16 | Output Scaling32 | Inputs | Input Param | Input Scaling16 | Input Scaling32 | Outputs | Output Param | Output Scaling16 | Output Scaling32
[21 empty] | ACS380 |  |  | ACS380 |  |  | ACS480 |  |  | ACS480 |  |  | ACS580 |  |  | ACS580 |  |  | ACS880 |  |  |  | ACS880 |  |  |  | DCS880 |  |  |  | DCS880
[21 empty] | Other |  |  | Other |  |  | Other |  |  | Other |  |  | Other |  |  | Other |  |  | Other |  |  |  | Other |  |  |  | Other |  |  |  | Other
[21 empty] | Motor speed used | 1.01 | 20000=Par46.01 | RO/DIO control word | 10.99 | 1=1 | Motor speed used | 1.01 | 20000=Par46.01 | RO/DIO control word | 10.99 | 1=1 | Motor speed used | 1.01 | 20000=Par46.01 | RO/DIO control word | 10.99 | 1=1 | Motor speed used | 1.01 | 20000=Par46.01 | 100=1rpm | RO/DIO control word | 10.99 | 1=1 | 1=1 | Used motor spd filt | 1.01 | 20000=Par46.01 | FW Manual | User control word1 | 6.100 | 1=1 | FW Manual
[21 empty] | Motor speed estimated | 1.02 | 20000=Par46.01 | AO1 data storage | 13.91 | 100=1mA | Motor speed estimated | 1.02 | 20000=Par46.01 | AO1 data storage | 13.91 | 100=1mA | Motor speed estimated | 1.02 | 20000=Par46.01 | AO1 data storage | 13.91 | 100=1mA | Motor speed estimated | 1.02 | 20000=Par46.01 | 100=1rpm | AO1 data storage | 13.91 | 100=1 | 100=1 | EMF spd filtered | 1.02 | 20000=Par46.01 | FW Manual | User control word2 | 6.101 | 1=1 | FW Manual
[17 empty] | 24 |  |  |  | Motor speed % | 1.03 | 20000=Par46.01 | Speed ref safe | 22.41 | 20000=Par46.01 | Motor speed % | 1.03 | 20000=Par46.01 | Speed ref safe | 22.41 | 20000=Par46.01 | Motor speed % | 1.03 | 20000=Par46.01 | AO2 data storage | 13.92 | 100=1mA | Motor speed % | 1.03 | 20000=Par46.01 | 100=1% | AO2 data storage | 13.92 | 100=1 | 100=1 | Tacho spd filtered | 1.03 | 20000=Par46.01 | FW Manual | RO/DIO control word | 10.99 | 1=1 | FW Manual
[14 empty] | 128.0.0.0 | 1 |  |  | Rockwell Drives |  |  | Encoder 1 speed filtered | 1.04 | 1=1 | Jogging 1 ref | 22.42 | 20000=Par46.01 | Encoder 1 speed filtered | 1.04 | 1=1 | Jogging 1 ref | 22.42 | 20000=Par46.01 | Output frequency | 1.06 | 20000=Par46.02 | Speed ref safe | 22.41 | 20000=Par46.01 | Encoder 1 speed filtered | 1.04 | 20000=Par46.01 | 100=1rpm | Cont mag command | 21.12 | 1=On | 1=On | OnBoard enc spd filt | 1.04 | 20000=Par46.01 | FW Manual | AO1 data storage | 13.91 | 100=1 | FW Manual
[14 empty] | 192.0.0.0 | 2 |  |  | Powerflex755 |  |  | Output frequency | 1.06 | 20000=Par46.02 | Jogging 2 ref | 22.43 | 20000=Par46.01 | Output frequency | 1.06 | 20000=Par46.02 | Jogging 2 ref | 22.43 | 20000=Par46.01 | Motor current | 1.07 | 10000=Par46.05 | Jogging 1 ref | 22.42 | 20000=Par46.01 | Encoder 2 speed filtered | 1.05 | 20000=Par46.01 | 100=1rpm | Speed share | 22.16 | 1000=1 | 1000=1 | Encoder 1 spd filt | 1.05 | 20000=Par46.01 | FW Manual | AO2 data storage | 13.92 | 100=1 | FW Manual
| 1 | Predefined by the VFD - 16bit | [9 empty] | Outputs | Inputs | 224.0.0.0 | 3 |  |  | Powerflex525 |  |  | Motor current | 1.07 | 10000=Par46.05 | Acceleration time 1 | 23.12 | 10=1s | Motor current | 1.07 | 10000=Par46.05 | Acceleration time 1 | 23.12 | 10=1s | Motor current % of motor nom | 1.08 | 1=1% | Jogging 2 ref | 22.43 | 20000=Par46.01 | Output frequency | 1.06 | 20000=Par46.02 | 100=1Hz | Speed ref safe | 22.41 | 20000=Par46.01 | 100=1rpm | Encoder 2 spd filt | 1.06 | 20000=Par46.01 | FW Manual | Speed reference | 22.07 | 20000=Par46.01 | FW Manual
| 2 | Customized by the PLC Programmer - 16bit | [6 empty] | Speed |  |  | #REF! | #REF! | 240.0.0.0 | 4 | [5 empty] | Motor current % of motor nom | 1.08 | 1=1% | Deceleration time 1 | 23.13 | 10=1s | Motor current % of motor nom | 1.08 | 1=1% | Deceleration time 1 | 23.13 | 10=1s | Motor current % of drive nom | 1.09 | 1=1% | Acceleration time 1 | 23.12 | 10=1s | Motor current | 1.07 | 10000=Par46.05 | 100=1A | Jogging 1 ref | 22.42 | 20000=Par46.01 | 100=1rpm | Speed change rate | 1.07 | 1=1rpm/s | FW Manual | Aux speed reference | 22.08 | 20000=Par46.01 | FW Manual
|  | Customized by the PLC Programmer - 32bit | [5 empty] | Vector | DTC |  |  | #REF! | #REF! | 248.0.0.0 | 5 | [5 empty] | Motor current % of drive nom | 1.09 | 1=1% | Acc time jogging | 23.20 | 10=1s | Motor current % of drive nom | 1.09 | 1=1% | Acc time jogging | 23.20 | 10=1s | Motor torque | 1.10 | 10000=Par46.03 | Deceleration time 1 | 23.13 | 10=1s | Motor current % of motor nom | 1.08 | 1=1% | 10=1% | Jogging 2 ref | 22.43 | 20000=Par46.01 | 100=1rpm | Motor current Amp | 1.10 | 1=1A | FW Manual | Speed share | 22.16 | 1000=1 | FW Manual
[8 empty] | Scalar (V/Hz) | Scalar (V/Hz) |  |  | #REF! | #REF! | 252.0.0.0 | 6 | [5 empty] | Motor torque | 1.10 | 10000=Par46.03 | Dec time jogging | 23.21 | 10=1s | Motor torque | 1.10 | 10000=Par46.03 | Dec time jogging | 23.21 | 10=1s | DC voltage | 1.11 | 10=1V | Acc time jogging | 23.20 | 10=1s | Motor torque | 1.10 | 10000=Par46.03 | 10=1% | Acceleration time 1 | 23.12 | 10=1s | 1000=1s | Motor torque filt | 1.17 | 10000=Par46.03 | FW Manual | Jogging 1 reference | 22.42 | 20000=Par46.01 | FW Manual
|  | 50.01 | 51.27 | Control Mode | Direction | Dir Param |  |  | Vector |  |  | #REF! | #REF! | 254.0.0.0 | 7 | [5 empty] | DC voltage | 1.11 | 10=1V | Shape time 1 | 23.32 | 10=1s | DC voltage | 1.11 | 10=1V | Shape time 1 | 23.32 | 10=1s | Output voltage | 1.13 | 1=1V | Dec time jogging | 23.21 | 10=1s | DC voltage | 1.11 | 10=1V | 100=1V | Deceleration time 1 | 23.13 | 10=1s | 1000=1s | Mains voltage | 1.20 | 10=1V | FW Manual | Jogging 2 reference | 22.43 | 20000=Par46.01 | FW Manual
| ACS380 | Enable | Configure | Scalar (V/Hz) | Request | 20.21 | 1 | ODVA ACDC Basic Profile |  |  |  | #REF! | #REF! | 255.0.0.0 | 8 | [5 empty] | Output voltage | 1.13 | 1=1V | Speed correction | 24.11 | 20000=Par46.01 | Output voltage | 1.13 | 1=1V | Speed correction | 24.11 | 20000=Par46.01 | Output power | 1.14 | 10000=Par46.04 | Shape time 1 | 23.32 | 10=1s | Output voltage | 1.13 | 1=1V | 1=1V | Shape time acc 1 | 23.16 | 10=1s | 1000=1s | Armature voltage | 1.21 | 10=1V | FW Manual | Speed ref safe | 22.46 | 20000=Par46.01 | FW Manual
| ACS480 | Enable | Configure | Scalar (V/Hz) | Request | 20.21 | 2 | ODVA ACDC Extended Profile |  |  |  | #REF! | #REF! | 255.128.0.0 | 9 | [5 empty] | Output power | 1.14 | 10000=Par46.04 | Freq acceleration time 1 | 28.72 | 10=1s | Output power | 1.14 | 10000=Par46.04 | Freq acceleration time 1 | 28.72 | 10=1s | Output power % of motor nom | 1.15 | 10=1% | Speed correction | 24.11 | 20000=Par46.01 | Output power | 1.14 | 10000=Par46.04 | 100=1unit | Shape time dec 1 | 23.18 | 10=1s | 1000=1s | Output power | 1.24 | 1=1kworHp | FW Manual | Accleration time1 | 23.12 | 10=1s | FW Manual
| ACS580 | Enable | Configure | Scalar (V/Hz) | Request | 20.21 | 3 | ABB Drives Profile |  |  |  | #REF! | #REF! | 255.192.0.0 | 10 | [5 empty] | Output power % of motor nom | 1.15 | 10=1% | Freq deceleration time 1 | 28.73 | 10=1s | Output power % of motor nom | 1.15 | 10=1% | Freq deceleration time 1 | 28.73 | 10=1s | Output power % of drive nom | 1.16 | 10=1% | Freq acceleration time 1 | 28.72 | 10=1s | Output power % of motor nom | 1.15 | 10=1% | 10=1% | Acc time jogging | 23.20 | 10=1s | 1000=1s | Output power % | 1.25 | 100=1% | FW Manual | Decleration time1 | 23.13 | 10=1s | FW Manual
| ACS880 | Option Slot 1 | Refresh | DTC | Selected | 20.24 | 4 | Transparent 16 Profile |  |  |  | #REF! | #REF! | 255.224.0.0 | 11 | [5 empty] | Output power % of drive nom | 1.16 | 10=1% | Shape time 1 | 28.82 | 10=1s | Output power % of drive nom | 1.16 | 10=1% | Shape time 1 | 28.82 | 10=1s | Motor shaft power | 1.17 | 10000=Par46.04 | Freq deceleration time 1 | 28.73 | 10=1s | Motor shaft power | 1.17 | 1=1unit | 100=1unit | Dec time jogging | 23.21 | 10=1s | 1000=1s | Reactive power % | 1.26 | 100=1% | FW Manual | Shape time acc 1 | 23.16 | 10=1s | FW Manual
| DCS880 | Option Slot 1 | Refresh | Speed | Enable Neg Spd | 20.24 | 5 | Transparent 32 Profile |  |  |  | #REF! | #REF! | 255.240.0.0 | 12
| ACH580 | Enable | Configure | Scalar (V/Hz) | Request | 20.21 | [5 empty] | #REF! | #REF! | 255.248.0.0 | 13
| ACQ580 | Enable | Configure | Scalar (V/Hz) | Request | 20.21 |  | Vector |  |  |  | 1 | 1 | 255.252.0.0 | 14 | [5 empty] | Inverter MWh motoring | 1.19 | 1=1MWh | Minimum frequency | 30.13 | 20000=Par46.02 | Inverter MWh motoring | 1.19 | 1=1MWh | Minimum frequency | 30.13 | 20000=Par46.02 | Inverter kWh motoring | 1.20 | 10=1kWh | Maximum speed | 30.12 | 20000=Par46.01 | Inverter kWh motoring | 1.20 | 10=1kWh | 10=1kWh | Freq deceleration time 1 | 28.73 | 10=1s | 1000=1s | Drive current | 1.40 | 100=1% | FW Manual | Dec time jogging | 23.21 | 10=1s | FW Manual
|  | Enable | Configure | Scalar (V/Hz) | Request | 20.21 | [5 empty] | 2 | 2 | 255.254.0.0 | 15 | [5 empty] | Inverter kWh motoring | 1.20 | 10=1kWh | Maximum frequency | 30.14 | 20000=Par46.02 | Inverter kWh motoring | 1.20 | 10=1kWh | Maximum frequency | 30.14 | 20000=Par46.02 | Flux actual % | 1.24 | 1=1% | Minimum frequency | 30.13 | 20000=Par46.02 | Flux actual % | 1.24 | 1=1% | 1=1% | Minimum speed | 30.11 | 20000=Par46.01 | 100=1rpm | Reactive current | 1.41 | 100=1% | FW Manual | Emergency stop time | 23.23 | 10=1s | FW Manual
[12 empty] | #REF! | #REF! | 255.255.0.0 | 16 | [5 empty] | Flux actual % | 1.24 | 1=1% | Maximum current | 30.17 | 1=1A | Flux actual % | 1.24 | 1=1% | Maximum current | 30.17 | 1=1A | Ambient temperature | 1.31 | 1=1º | Maximum frequency | 30.14 | 20000=Par46.02 | Ambient temperature | 1.31 | 1=1º | 10=1º | Maximum speed | 30.12 | 20000=Par46.01 | 100=1rpm | Current ripple | 1.50 | 100=1% | FW Manual | Speed correction | 24.11 | 20000=Par46.01 | FW Manual
[21 empty] | Nom Torque Scale | 1.30 | 1=100 | Minimum torque 1 | 30.19 | 10000=Par46.03 | Nom Torque Scale | 1.30 | 1=100 | Minimum torque 1 | 30.19 | 10000=Par46.03 | Cumulative inverter energy | 1.54 | 10=1kWh | Maximum current | 30.17 | 1=1A | Inverter GWh regenerating | 1.32 | 1=1GWh | 1=1GWh | Minimum frequency | 30.13 | 20000=Par46.02 | 100=1Hz | 12pulse serial arm V | 1.60 | 10=1V | FW Manual | Ext torque ref 1 | 26.07 | 10000=Par46.03 | FW Manual
| ACS380 | ACS480 | ACS580 | ACS880 | DCS880 | ACH580 | ACQ580 | [13 empty] | Cumulative inverter energy | 1.54 | 10=1kWh | Maximum torque 1 | 30.20 | 10000=Par46.03 | Cumulative inverter energy | 1.54 | 10=1kWh | Maximum torque 1 | 30.20 | 10000=Par46.03 | Inverter GWh counter | 1.55 | 1=1GWh | Minimum torque 1 | 30.19 | 10000=Par46.03 | Inverter MWh regenerating | 1.33 | 1=1MWh | 1=1MWh | Maximum frequency | 30.14 | 20000=Par46.02 | 100=1Hz | 12pulse parallel Amp | 1.61 | 1=1A | FW Manual | Ext torque ref 2 | 26.08 | 10000=Par46.03 | FW Manual
| Predefined by the VFD - 16bit | Predefined by the VFD - 16bit | Predefined by the VFD - 16bit | Predefined by the VFD - 16bit | Predefined by the VFD - 16bit | Predefined by the VFD - 16bit | Predefined by the VFD - 16bit | [6 empty] | 255.255.224.0 | 19 | [5 empty] | Inverter GWh counter | 1.55 | 1=1GWh | Power motoring limit | 30.26 | 1=1% | Inverter GWh counter | 1.55 | 1=1GWh | Power motoring limit | 30.26 | 1=1% | Inverter MWh counter | 1.56 | 1=1MWh | Maximum torque 1 | 30.20 | 10000=Par46.03 | Inverter kWh regenerating | 1.34 | 10=1kWh | 1=1kWh | Maximum start current | 30.16 | 1=1A | 100=1A | Mains voltage fast | 1.70 | 100=1% | FW Manual | Arm cur ref external | 27.23 | 100=1% | FW Manual
[14 empty] | 255.255.240.0 | 20 | [5 empty] | Inverter MWh counter | 1.56 | 1=1MWh | Power generating limit | 30.27 | 1=1% | Inverter MWh counter | 1.56 | 1=1MWh | Power generating limit | 30.27 | 1=1% | Inverter kWh counter | 1.57 | 10=1kWh | Power motoring limit | 30.26 | 1=1% | Mot - regen energy GWh | 1.35 | 1=1GWh | 1=1GWh | Maximum current | 30.17 | 1=1A | 100=1A | Arm voltage fast | 1.71 | 100=1% | FW Manual | EMF volt ext ref | 28.19 | 100=1% | FW Manual
[14 empty] | 255.255.248.0 | 21 | [5 empty] | Inverter kWh counter | 1.57 | 10=1kWh | Motor ambient temperature | 35.50 | 1=1º | Inverter kWh counter | 1.57 | 10=1kWh | Motor ambient temperature | 35.50 | 1=1º | Cumulative inverter energy rst | 1.58 | 10=1kWh | Power generating limit | 30.27 | 1=1% | Mot - regen energy MWh | 1.36 | 1=1mWh | 1=1mWh | Minimum torque 1 | 30.19 | 10000=Par46.03 | 10=1% | Used spd ref fast | 1.72 | 20000=Par46.01 | FW Manual | Minimum speed | 30.11 | 20000=Par46.01 | FW Manual
[14 empty] | 255.255.252.0 | 22 | [5 empty] | Cumulative inverter energy rst | 1.58 | 10=1kWh | Set 1 internal setpoint 1 | 40.21 | 1=1unit | Cumulative inverter energy rst | 1.58 | 10=1kWh | Set 1 internal setpoint 1 | 40.21 | 1=1unit | Abs motor speed used | 1.61 | 1=1rpm | Motor ambient temperature | 35.50 | 1=1º | Mot - regen energy kWh | 1.37 | 10=1kWh | 1=1kWh | Maximum torque 1 | 30.20 | 10000=Par46.03 | 10=1% | Used spd fdbk fast | 1.73 | 20000=Par46.01 | FW Manual | Maximum speed | 30.12 | 20000=Par46.01 | FW Manual
[10 empty] | 50.01 selections: |  |  |  | 255.255.254.0 | 23 | [5 empty] | Abs motor speed used | 1.61 | 1=1rpm | Set 1 internal setpoint 2 | 40.22 | 1=1unit | Abs motor speed used | 1.61 | 1=1rpm | Set 1 internal setpoint 2 | 40.22 | 1=1unit | Abs motor speed % | 1.62 | 10=1% | Set 1 internal setpoint 1 | 40.21 | 1=1unit | Abs motor speed used | 1.61 | 20000=Par46.01 | 100=1rpm | Power motoring limit | 30.26 | 1=1% | 100=1% | Used current ref fast | 1.74 | 100=1% | FW Manual | Spd control min torq | 30.13 | 10000=Par46.03 | FW Manual
| 1 | ODVA ACDC Basic Profile |  |  | 4 |  |  |  |  | Option Slot 1 |  |  |  | 255.255.255.0 | 24 | [5 empty] | Abs motor speed % | 1.62 | 10=1% | Set 1 internal setpoint 3 | 40.23 | 1=1unit | Abs motor speed % | 1.62 | 10=1% | Set 1 internal setpoint 3 | 40.23 | 1=1unit | Abs output frequency | 1.63 | 1=1Hz | Set 1 internal setpoint 2 | 40.22 | 1=1unit | Abs motor speed % | 1.62 | 10=1% | 100=1% | Power generating limit | 30.27 | 1=1% | 100=1% | Motor current fast | 1.75 | 100=1% | FW Manual | Spd control max torq | 30.14 | 10000=Par46.03 | FW Manual
| 2 | ODVA ACDC Extended Profile |  |  | 5 |  |  |  |  | Option Slot 2 |  |  |  | 255.255.255.128 | 25 | [5 empty] | Abs output frequency | 1.63 | 1=1Hz | Set 1 internal setpoint 0 | 40.24 | 1=1unit | Abs output frequency | 1.63 | 1=1Hz | Set 1 internal setpoint 0 | 40.24 | 1=1unit | Abs motor torque | 1.64 | 1=1% | Set 1 internal setpoint 3 | 40.23 | 1=1unit | Abs output frequency | 1.63 | 20000=Par46.02 | 100=1Hz | Motor ambient temperature | 35.50 | 1=1º | 1=1º | Firing Angle fast | 1.76 | 100=1° | FW Manual | Minimum torque 1 | 30.19 | 10000=Par46.03 | FW Manual
| 3 | ABB Drives Profile |  |  | 6 |  |  |  |  | Option Slot 3 |  |  |  | 255.255.255.192 | 26 | [5 empty] | Abs motor torque | 1.64 | 1=1% | Feedback data storage | 40.91 | 100=1 | Abs motor torque | 1.64 | 1=1% | Feedback data storage | 40.91 | 100=1 | Abs output power | 1.65 | 1=1kW | Set 1 internal setpoint 0 | 40.24 | 1=1unit | Abs motor torque | 1.64 | 10000=Par46.03 | 10=1% | Set 1 internal setpoint 1 | 40.21 | 1=1unit | 100=1unit | M1 fld cur ref fast | 1.77 | 100=1% | FW Manual | Maximum torque 1 | 30.20 | 10000=Par46.03 | FW Manual
| 4 | Transparent 16 Profile |  |  | 2 |  |  |  |  | Enable |  |  |  | 255.255.255.224 | 27 | [5 empty] | Abs output power | 1.65 | 1=1kW | Setpoint data storage | 40.92 | 100=1 | Abs output power | 1.65 | 1=1kW | Setpoint data storage | 40.92 | 100=1 | Abs output power % motor nom | 1.66 | 1=1% | Feedback data storage | 40.91 | 100=1 | Abs output power | 1.65 | 1=1unit | 100=1unit | Set 1 internal setpoint 2 | 40.22 | 1=1unit | 100=1unit | M1 fld current fast | 1.78 | 100=1% | FW Manual | M1 cur lim bridge2 | 30.34 | 100=1% | FW Manual
| 5 | Transparent 32 Profile |  |  | 3 | [8 empty] | 255.255.255.240 | 28 | [5 empty] | Abs output power % motor nom | 1.66 | 1=1% | Brake open torque | 44.10 | 10000=Par46.03 | Abs output power % motor nom | 1.66 | 1=1% | Brake open torque | 44.10 | 10000=Par46.03 | Abs output power % drive nom | 1.67 | 1=1% | Setpoint data storage | 40.92 | 100=1 | Abs output power % motor nom | 1.66 | 10=1% | 10=1% | Set 1 internal setpoint 3 | 40.23 | 1=1unit | 100=1unit | M2 fld cur ref fast | 1.79 | 100=1% | FW Manual | M1 cur lim bridge1 | 30.35 | 100=1% | FW Manual
[14 empty] | 255.255.255.248 | 29 | [5 empty] | Abs output power % drive nom | 1.67 | 1=1% | DataStorage 1 int32 | 47.11 | 1=1 | Abs output power % drive nom | 1.67 | 1=1% | DataStorage 1 int32 | 47.11 | 1=1 | Abs motor shaft power | 1.68 | 1=1kW | DataStorage 1 int32 | 47.11 | 1=1 | Abs motor shaft power | 1.68 | 1=1unit | 100=1unit | Set 1 internal setpoint 4 | 40.24 | 1=1unit | 100=1unit | M2 fld current fast | 1.80 | 100=1% | FW Manual | Motor ambient temp1 | 35.50 | 1=1°C or F | FW Manual
[14 empty] | 255.255.255.252 | 30 | [5 empty] | Abs motor shaft power | 1.68 | 1=1kW | DataStorage 2 int32 | 47.12 | 1=1 | Abs motor shaft power | 1.68 | 1=1kW | DataStorage 2 int32 | 47.12 | 1=1 | Tripping fault | 4.01 | 1=1 | DataStorage 2 int32 | 47.12 | 1=1 | U-phase RMS current | 1.72 | 10000=Par46.05 | 100=1A | Feedback data storage | 40.91 | 100=1 | 100=1 | Tripping Fault | 4.01 | 1=1 | FW Manual | Motor ambient temp2 | 35.58 | 1=1°C or F | FW Manual
[14 empty] | 255.255.255.254 | 31 | [5 empty] | Tripping fault | 4.01 | 1=1 | DataStorage 3 int32 | 47.13 | 1=1 | Tripping fault | 4.01 | 1=1 | DataStorage 3 int32 | 47.13 | 1=1 | Active warning 1 | 4.06 | 1=1 | DataStorage 3 int32 | 47.13 | 1=1 | V-phase RMS current | 1.73 | 10000=Par46.05 | 100=1A | Setpoint data storage | 40.92 | 100=1 | 100=1 | Active Warning | 4.06 | 1=1 | FW Manual | Set 1 internal setpoint 1 | 40.21 | 1=1unit | FW Manual
[21 empty] | Active warning 1 | 4.06 | 1=1 | DataStorage 4 int32 | 47.14 | 1=1 | Active warning 1 | 4.06 | 1=1 | DataStorage 4 int32 | 47.14 | 1=1 | Latest fault | 4.11 | 1=1 | DataStorage 4 int32 | 47.14 | 1=1 | W-phase RMS current | 1.74 | 10000=Par46.05 | 100=1A | Brake open torque | 44.10 | 10000=Par46.03 | 10=1% | Latest fault | 4.11 | 1=1 | FW Manual | Set 1 internal setpoint 2 | 40.22 | 1=1unit | FW Manual
[21 empty] | Latest fault | 4.11 | 1=1 | DataStorage 1 int16 | 47.21 | 1=1 | Latest fault | 4.11 | 1=1 | DataStorage 1 int16 | 47.21 | 1=1 | Latest warning | 4.16 | 1=1 | DataStorage 1 int16 | 47.21 | 1=1 | Tripping fault | 4.01 | 1=1 | 1=1 | DataStorage 1 int32 | 47.11 | 1=1 | 1=1 | Latest warning | 4.16 | 1=1 | FW Manual | Set 1 internal setpoint 3 | 40.23 | 1=1unit | FW Manual
[21 empty] | Latest warning | 4.16 | 1=1 | DataStorage 2 int16 | 47.22 | 1=1 | Latest warning | 4.16 | 1=1 | DataStorage 2 int16 | 47.22 | 1=1 | On-time counter | 5.01 | 1=1day | DataStorage 2 int16 | 47.22 | 1=1 | Active warning 1 | 4.06 | 1=1 | 1=1 | DataStorage 2 int32 | 47.12 | 1=1 | 1=1 | Fault word 1 | 4.21 | 1=1 | FW Manual | Set 1 internal setpoint 4 | 40.24 | 1=1unit | FW Manual
[21 empty] | On-time counter | 5.01 | 1=1day | DataStorage 3 int16 | 47.23 | 1=1 | On-time counter | 5.01 | 1=1day | DataStorage 3 int16 | 47.23 | 1=1 | Run-time counter | 5.02 | 1=1day | DataStorage 3 int16 | 47.23 | 1=1 | Latest fault | 4.11 | 1=1 | 1=1 | DataStorage 3 int32 | 47.13 | 1=1 | 1=1 | Fault word 2 | 4.22 | 1=1 | FW Manual | Feedback data storage | 40.91 | 100=1 | FW Manual
[21 empty] | Run-time counter | 5.02 | 1=1day | DataStorage 4 int16 | 47.24 | 1=1 | Run-time counter | 5.02 | 1=1day | DataStorage 4 int16 | 47.24 | 1=1 | Fan on-time counter | 5.04 | 1=1day | DataStorage 4 int16 | 47.24 | 1=1 | Latest warning | 4.16 | 1=1 | 1=1 | DataStorage 4 int32 | 47.14 | 1=1 | 1=1 | Fault word 3 | 4.23 | 1=1 | FW Manual | Setpoint data storage | 40.92 | 100=1 | FW Manual
[10 empty] | Input Data Selection Formula | [10 empty] | Fan on-time counter | 5.04 | 1=1day | Clear fault and event logger | 96.51 | 1=reset | Fan on-time counter | 5.04 | 1=1day | Clear fault and event logger | 96.51 | 1=reset | Inverter temperature | 5.11 | 1=1% | Clear fault and event logger | 96.51 | 1=reset | Fault word 1 | 4.21 | 1=1 | 1=1 | DataStorage 1 int16 | 47.21 | 1=1 | 1=1 | User Fault Word | 4.25 | 1=1 | FW Manual | Brake open torque | 44.1 | 10000=Par46.03 | FW Manual
|  |  | Speed or Freq Scaling Lookup | [6 empty] | Main status word | [10 empty] | Inverter temperature | 5.11 | 1=1% | Disable adaptive program | 96.70 | 1=disable | Inverter temperature | 5.11 | 1=1% | Disable adaptive program | 96.70 | 1=disable | Main status word | 6.11 | 1=1 | Disable adaptive program | 96.70 | 1=disable | Fault word 2 | 4.22 | 1=1 | 1=1 | DataStorage 2 int16 | 47.22 | 1=1 | 1=1 | Warning word 1 | 4.31 | 1=1 | FW Manual | DataStorage 1 int32 | 47.11 | 1=1 | FW Manual
[10 empty] | Output Data Selection Formala | [10 empty] | Main status word | 6.11 | 1=1 | Motor nominal current | 99.06 | 1=1A | Main status word | 6.11 | 1=1 | Motor nominal current | 99.06 | 1=1A | Drive status word 1 | 6.16 | 1=1 | Motor nominal current | 99.06 | 1=1A | Warning word 1 | 4.31 | 1=1 | 1=1 | DataStorage 3 int16 | 47.23 | 1=1 | 1=1 | Warning word 2 | 4.32 | 1=1 | FW Manual | DataStorage 2 int32 | 47.12 | 1=1 | FW Manual
|  | CtrlMode | T16 | T32 | ODVA Basic | ODVA Ext | ABB |  |  | Motor nominal voltage | [10 empty] | Drive status word 1 | 6.16 | 1=1 | Motor nominal voltage | 99.07 | 10=1V | Drive status word 1 | 6.16 | 1=1 | Motor nominal voltage | 99.07 | 10=1V | Drive status word 2 | 6.17 | 1=1 | Motor nominal voltage | 99.07 | 10=1V | Warning word 2 | 4.32 | 1=1 | 1=1 | DataStorage 4 int16 | 47.24 | 1=1 | 1=1 | Warning word 3 | 4.33 | 1=1 | FW Manual | DataStorage 3 int32 | 47.13 | 1=1 | FW Manual
|  | Scalar (V/Hz) | 1=1Hz | 100=1Hz | 1=1Hz | 1=1Hz | 20000=Par46.02 | [13 empty] | Drive status word 2 | 6.17 | 1=1 | Motor nominal frequency | 99.08 | 10=1Hz | Drive status word 2 | 6.17 | 1=1 | Motor nominal frequency | 99.08 | 10=1Hz | Start inhibit status word | 6.18 | 1=1 | Motor nominal frequency | 99.08 | 10=1Hz | On-time counter | 5.01 | 1=1day | 1=1day | DataStorage 5 int16 | 47.25 | 1=1 | 1=1 | User warning word | 4.35 | 1=1 | FW Manual | DataStorage 4 int32 | 47.14 | 1=1 | FW Manual
|  | Vector | 1=1rpm | 100=1rpm | 1=1rpm | 1=1rpm | 20000=Par46.01 | [13 empty] | Start inhibit status word | 6.18 | 1=1 | Motor nominal speed | 99.09 | 1=1rpm | Start inhibit status word | 6.18 | 1=1 | Motor nominal speed | 99.09 | 1=1rpm | Speed control status word | 6.19 | 1=1 | Motor nominal speed | 99.09 | 1=1rpm | Run-time counter | 5.02 | 1=1day | 1=1day | DataStorage 6 int16 | 47.26 | 1=1 | 1=1 | On-time counter | 5.01 | 1=1day | FW Manual | DataStorage 1 int16 | 47.21 | 1=1 | FW Manual
|  | DTC | 1=1rpm | 100=1rpm | 1=1rpm | 1=1rpm | 20000=Par46.01 | [13 empty] | Speed control status word | 6.19 | 1=1 | Motor nominal power | 99.10 | 1=1unit | Speed control status word | 6.19 | 1=1 | Motor nominal power | 99.10 | 1=1unit | Drive status word 3 | 6.21 | 1=1 | Motor nominal power | 99.10 | 1=1unit | Fan on-time counter | 5.04 | 1=1day | 1=1day | DataStorage 7 int16 | 47.27 | 1=1 | 1=1 | Run-time counter | 5.02 | 1=1day | FW Manual | DataStorage 2 int16 | 47.22 | 1=1 | FW Manual
|  | Speed | 1=1rpm | 100=1rpm | 1=1rpm | 1=1rpm | 20000=Par46.01 | [13 empty] | Drive status word 3 | 6.21 | 1=1 | ID run requested | 99.13 | 1=1 | Drive status word 3 | 6.21 | 1=1 | ID run requested | 99.13 | 1=1 | Drive rating id | 7.03 | " " | ID run requested | 99.13 | 1=1 | Inverter temperature | 5.11 | 1=1% | 10=1% | DataStorage 8 int16 | 47.28 | 1=1 | 1=1 | Fan on-time counter | 5.04 | 1=1day | FW Manual | DataStorage 3 int16 | 47.23 | 1=1 | FW Manual
[21 empty] | Drive rating id | 7.03 | " " |  |  |  | Drive rating id | 7.03 | " " |  |  |  | Firmware version | 7.05 | " " |  |  |  | Main fan service counter | 5.41 | 1=1% | 1=1% | Force master | 60.15 | 1=True | 1=True | Control board temp | 5.10 | 1=1°C or F | FW Manual | DataStorage 4 int16 | 47.24 | 1=1 | FW Manual
[21 empty] | Firmware version | 7.05 | " " |  |  |  | Firmware version | 7.05 | " " |  |  |  | Adaptive program status | 7.30 | 1=1 |  |  |  | Aux. fan service counter | 5.42 | 1=1% | 1=1% | Force follower | 60.16 | 1=True | 1=True | Ch1 bridge temp | 5.11 | 1=1°C or F | FW Manual | DataStorage 5 int16 | 47.25 | 1=1 | FW Manual
|  | Column # | #N/A | [17 empty] | Adaptive program status | 7.30 | 1=1 |  |  |  | Adaptive program status | 7.30 | 1=1 |  |  |  | DI delayed status | 10.02 | 1=1 |  |  |  | Main status word | 6.11 | 1=1 | 1=1 | Clear fault and event logger | 96.51 | 1=reset | 1=reset | Main fan service cntr | 5.41 | 1=1% | FW Manual | DataStorage 6 int16 | 47.26 | 1=1 | FW Manual
[21 empty] | DI delayed status | 10.02 | 1=1 |  |  |  | DI delayed status | 10.02 | 1=1 |  |  |  | RO status | 10.21 | 1=1 |  |  |  | Drive status word 1 | 6.16 | 1=1 | 1=1 | Disable adaptive program | 96.70 | 1=disable | 1=disable | Main status word | 6.15 | 1=1 | FW Manual | DataStorage 7 int16 | 47.27 | 1=1 | FW Manual
|  |  | #REF! | [17 empty] | RO status | 10.21 | 1=1 |  |  |  | RO status | 10.21 | 1=1 |  |  |  | AI1 actual value | 12.11 | 1000=1mAorV |  |  |  | Drive status word 2 | 6.17 | 1=1 | 1=1 | Motor nominal current | 99.06 | 1=1A | 10=1A | Drive status word1 | 6.16 | 1=1 | FW Manual | DataStorage 8 int16 | 47.28 | 1=1 | FW Manual
[21 empty] | AI1 actual value | 12.11 | 1000=1mAorV |  |  |  | AI1 actual value | 12.11 | 1000=1mAorV |  |  |  | AI2 actual value | 12.21 | 1000=1mAorV |  |  |  | Start inhibit status word | 6.18 | 1=1 | 1=1 | Motor nominal voltage | 99.07 | 10=1V | 10=1V | Drive status word2 | 6.17 | 1=1 | FW Manual | Force master | 60.15 | 1=True | FW Manual
[21 empty] | AI2 actual value | 12.21 | 1000=1mAorV |  |  |  | AI2 actual value | 12.21 | 1000=1mAorV |  |  |  | AO1 actual value | 13.11 | 1=1mA |  |  |  | Speed control status word | 6.19 | 1=1 | 1=1 | Motor nominal frequency | 99.08 | 10=1Hz | 10=1Hz | Drive status word3 | 6.18 | 1=1 | FW Manual | Force follower | 60.16 | 1=True | FW Manual
[21 empty] | AO1 actual value | 13.11 | 1=1mA |  |  |  | AO1 actual value | 13.11 | 1=1mA |  |  |  | AO2 actual value | 13.21 | 1=1mA |  |  |  | Drive status word 3 | 6.21 | 1=1 | 1=1 | Motor nominal speed | 99.09 | 1=1rpm | 1=1rpm | Drive inhibit status | 6.19 | 1=1 | FW Manual | Pos cntr init val int | 90.76 | 1=1 | FW Manual
[21 empty] | Speed ref unlimited | 22.01 | 20000=Par46.01 |  |  |  | Speed ref unlimited | 22.01 | 20000=Par46.01 |  |  |  | Speed ref unlimited | 22.01 | 20000=Par46.01 |  |  |  | User status word 1 | 6.50 | 1=1 | 1=1 | Motor nominal power | 99.10 | 1=1unit | 100=1unit | Run inhibit status w | 6.20 | 1=1 | FW Manual | Pos cntr init cmd | 90.86 | 1=True | FW Manual
[21 empty] | Speed ref ramp input | 23.01 | 20000=Par46.01 |  |  |  | Speed ref ramp input | 23.01 | 20000=Par46.01 |  |  |  | Speed ref ramp input | 23.01 | 20000=Par46.01 |  |  |  | Drive rating id | 7.03 | " " | " " | ID run requested | 99.13 | 1=1 | 1=1 | Spd ctrl status word | 6.21 | 1=1 | FW Manual | Reset pos cntr init | 90.88 | 1=True | FW Manual
[21 empty] | Speed ref ramp output | 23.02 | 20000=Par46.01 |  |  |  | Speed ref ramp output | 23.02 | 20000=Par46.01 |  |  |  | Speed ref ramp output | 23.02 | 20000=Par46.01 |  |  |  | Firmware version | 7.05 | " " | " " |  |  |  |  | User status word 1 | 6.50 | 1=1 | FW Manual | Parameter save | 96.16 | 1=Save | FW Manual
[21 empty] | Used speed reference | 24.01 | 20000=Par46.01 |  |  |  | Used speed reference | 24.01 | 20000=Par46.01 |  |  |  | Used speed reference | 24.01 | 20000=Par46.01 |  |  |  | Adaptive program status | 7.30 | 1=1 | 1=1 |  |  |  |  | Drive rating ID set | 7.03 | 1=1 | FW Manual | Clear fault and event logger | 96.51 | 1=reset | FW Manual
[21 empty] | Used speed feedback | 24.02 | 20000=Par46.01 |  |  |  | Used speed feedback | 24.02 | 20000=Par46.01 |  |  |  | Used speed feedback | 24.02 | 20000=Par46.01 |  |  |  | DI delayed status | 10.02 | 1=1 | 1=1 |  |  |  |  | Firmware version | 7.05 | 1=1 | FW Manual | Disable adaptive program | 96.70 | 1=disable | FW Manual
[21 empty] | Speed error filtered | 24.03 | 20000=Par46.01 |  |  |  | Speed error filtered | 24.03 | 20000=Par46.01 |  |  |  | Speed error filtered | 24.03 | 20000=Par46.01 |  |  |  | RO status | 10.21 | 1=1 | 1=1 |  |  |  |  | Adaptive program status | 7.30 | 1=1 | FW Manual | Nom Mains Volt | 99.10 | 10=1V | FW Manual
[21 empty] | Frequency ref ramp input | 28.01 | 20000=Par46.02 |  |  |  | Frequency ref ramp input | 28.01 | 20000=Par46.02 |  |  |  | Frequency ref ramp input | 28.01 | 20000=Par46.02 |  |  |  | DIO delayed status | 11.02 | 1=1 | 1=1 |  |  |  |  | DI delayed status | 10.02 | 1=1 | FW Manual | M1 nom Arm Amp | 99.11 | 1=1A | FW Manual
[21 empty] | Frequency ref ramp output | 28.02 | 20000=Par46.02 |  |  |  | Frequency ref ramp output | 28.02 | 20000=Par46.02 |  |  |  | Frequency ref ramp output | 28.02 | 20000=Par46.02 |  |  |  | AI1 actual value | 12.11 | 1000=1mAorV | 1000=1 |  |  |  |  | RO status | 10.21 | 1=1 | FW Manual | M1 nom voltage | 99.12 | 10=1V | FW Manual
[21 empty] | Frequency ref unlimited | 28.97 | 20000=Par46.02 |  |  |  | Frequency ref unlimited | 28.97 | 20000=Par46.02 |  |  |  | Frequency ref unlimited | 28.97 | 20000=Par46.02 |  |  |  | AI2 actual value | 12.21 | 1000=1mAorV | 1000=1 |  |  |  |  | DIO delayed status | 11.02 | 1=1 | FW Manual | M1 nom field Amp | 99.13 | 10=1A | FW Manual
[21 empty] | Limit word 1 | 30.01 | 1=1 |  |  |  | Limit word 1 | 30.01 | 1=1 |  |  |  | Limit word 1 | 30.01 | 1=1 |  |  |  | AO1 actual value | 13.11 | 1=1mA | 1000=1mA |  |  |  |  | AI1 actual value | 12.11 | 1000=1mAorV | FW Manual | M1 nom speed | 99.14 | 20000=Par46.01 | FW Manual
[21 empty] | Torque limit status | 30.02 | 1=1 |  |  |  | Torque limit status | 30.02 | 1=1 |  |  |  | Torque limit status | 30.02 | 1=1 |  |  |  | AO2 actual value | 13.21 | 1=1mA | 1000=1mA |  |  |  |  | AI2 actual value | 12.21 | 1000=1mAorV | FW Manual | Tuning Request | 99.20 | 1=1 | FW Manual
[21 empty] | Supervision status | 32.01 | 1=1 |  |  |  | Supervision status | 32.01 | 1=1 |  |  |  | Supervision status | 32.01 | 1=1 |  |  |  | Speed ref unlimited | 22.01 | 20000=Par46.01 | 100=1rpm |  |  |  |  | AO1 actual value | 13.11 | 1000=1mAorV | FW Manual
[21 empty] | Motor estimated temperature | 35.01 | 1=1º |  |  |  | Motor estimated temperature | 35.01 | 1=1º |  |  |  | Motor estimated temperature | 35.01 | 1=1º |  |  |  | Speed ref ramp input | 23.01 | 20000=Par46.01 | 100=1rpm |  |  |  |  | AO2 actual value | 13.21 | 1000=1V | FW Manual
[21 empty] | Measured temperature 1 | 35.02 | 1=1º |  |  |  | Measured temperature 1 | 35.02 | 1=1º |  |  |  | Measured temperature 1 | 35.02 | 1=1º |  |  |  | Speed ref ramp output | 23.02 | 20000=Par46.01 | 100=1rpm |  |  |  |  | Speed ref unlimited | 22.01 | 20000=Par46.01 | FW Manual
[21 empty] | Measured temperature 2 | 35.03 | 1=1º |  |  |  | Measured temperature 2 | 35.03 | 1=1º |  |  |  | Measured temperature 2 | 35.03 | 1=1º |  |  |  | Used speed reference | 24.01 | 20000=Par46.01 | 100=1rpm |  |  |  |  | Speed ref ramp input | 23.01 | 20000=Par46.01 | FW Manual
[21 empty] | ULC output status word | 37.01 | 1=1 |  |  |  | ULC output status word | 37.01 | 1=1 |  |  |  | ULC output status word | 37.01 | 1=1 |  |  |  | Used speed feedback | 24.02 | 20000=Par46.01 | 100=1rpm |  |  |  |  | Speed ref ramp output | 23.02 | 20000=Par46.01 | FW Manual
[21 empty] | Process PID output actual | 40.01 | 1=1% |  |  |  | Process PID output actual | 40.01 | 1=1% |  |  |  | Process PID output actual | 40.01 | 1=1% |  |  |  | Speed error filtered | 24.03 | 20000=Par46.01 | 100=1rpm |  |  |  |  | Used speed reference | 24.01 | 20000=Par46.01 | FW Manual
[21 empty] | Process PID feedback actual | 40.02 | 1=1unit |  |  |  | Process PID feedback actual | 40.02 | 1=1unit |  |  |  | Process PID feedback actual | 40.02 | 1=1unit |  |  |  | Frequency ref ramp input | 28.01 | 20000=Par46.02 | 100=1Hz |  |  |  |  | Used speed feedback | 24.02 | 20000=Par46.01 | FW Manual
[21 empty] | Process PID setpoint actual | 40.03 | 1=1unit |  |  |  | Process PID setpoint actual | 40.03 | 1=1unit |  |  |  | Process PID setpoint actual | 40.03 | 1=1unit |  |  |  | Frequency ref ramp output | 28.02 | 20000=Par46.02 | 100=1Hz |  |  |  |  | Speed error filtered | 24.03 | 20000=Par46.01 | FW Manual
[18 empty] | Custom Input | Custom Output |  | Process PID status word | 40.06 | 1=1 |  |  |  | Process PID status word | 40.06 | 1=1 |  |  |  | Process PID status word | 40.06 | 1=1 |  |  |  | Frequency ref unlimited | 28.97 | 20000=Par46.02 | 100=1Hz |  |  |  |  | Torque reference used | 26.02 | 10000=Par46.03 | FW Manual
[18 empty] | #REF! | #REF! |  | Braking resistor temperature | 43.01 | 1=1% |  |  |  | Braking resistor temperature | 43.01 | 1=1% |  |  |  | Braking resistor temperature | 43.01 | 1=1% |  |  |  | Limit word 1 | 30.01 | 1=1 | 1=1 |  |  |  |  | Motor peak current | 27.06 | 100=1% | FW Manual
[18 empty] | #REF! | #REF! |  | Brake control status | 44.01 | 1=1 |  |  |  | Brake control status | 44.01 | 1=1 |  |  |  | Brake control status | 44.01 | 1=1 |  |  |  | Torque limit status | 30.02 | 1=1 | 1=1 |  |  |  |  | Limit word 1 | 30.01 | 1=1 | FW Manual
[18 empty] | #REF! | #REF! |  | DataStorage 1 int32 | 47.11 | 1=1 |  |  |  | DataStorage 1 int32 | 47.11 | 1=1 |  |  |  | DataStorage 1 int32 | 47.11 | 1=1 |  |  |  | Supervision status | 32.01 | 1=1 | 1=1 |  |  |  |  | Torque limit status | 30.02 | 1=1 | FW Manual
[18 empty] | #REF! | #REF! |  | DataStorage 2 int32 | 47.12 | 1=1 |  |  |  | DataStorage 2 int32 | 47.12 | 1=1 |  |  |  | DataStorage 2 int32 | 47.12 | 1=1 |  |  |  | Motor estimated temperature | 35.01 | 1=1º | 1=1º |  |  |  |  | Supervision status | 32.01 | 1=1 | FW Manual
[18 empty] | #REF! | #REF! |  | DataStorage 3 int32 | 47.13 | 1=1 |  |  |  | DataStorage 3 int32 | 47.13 | 1=1 |  |  |  | DataStorage 3 int32 | 47.13 | 1=1 |  |  |  | Measured temperature 1 | 35.02 | 1=1º | 1=1º |  |  |  |  | Motor estimated temperature | 35.01 | 1=1ºCorF | FW Manual
[18 empty] | #REF! | #REF! |  | DataStorage 4 int32 | 47.14 | 1=1 |  |  |  | DataStorage 4 int32 | 47.14 | 1=1 |  |  |  | DataStorage 4 int32 | 47.14 | 1=1 |  |  |  | Measured temperature 2 | 35.03 | 1=1º | 1=1º |  |  |  |  | Measured temperature 1 | 35.02 | 1=1ºCorF | FW Manual
[18 empty] | #REF! | #REF! |  | DataStorage 1 int16 | 47.21 | 1=1 |  |  |  | DataStorage 1 int16 | 47.21 | 1=1 |  |  |  | DataStorage 1 int16 | 47.21 | 1=1 |  |  |  | ULC output status word | 37.01 | 1=1 | 1=1 |  |  |  |  | Measured temperature 2 | 35.04 | 1=1ºCorF | FW Manual
[18 empty] | #REF! | #REF! |  | DataStorage 2 int16 | 47.22 | 1=1 |  |  |  | DataStorage 2 int16 | 47.22 | 1=1 |  |  |  | DataStorage 2 int16 | 47.22 | 1=1 |  |  |  | Process PID output actual | 40.01 | 1=1% | 100=1unit |  |  |  |  | Motor ambient temp | 35.50 | 1=1ºCorF | FW Manual
[18 empty] | #REF! | #REF! |  | DataStorage 3 int16 | 47.23 | 1=1 |  |  |  | DataStorage 3 int16 | 47.23 | 1=1 |  |  |  | DataStorage 3 int16 | 47.23 | 1=1 |  |  |  | Process PID feedback actual | 40.02 | 1=1unit | 100=1unit |  |  |  |  | ULC output status word | 37.01 | 1=1 | FW Manual
[18 empty] | #REF! | #REF! |  | DataStorage 4 int16 | 47.24 | 1=1 |  |  |  | DataStorage 4 int16 | 47.24 | 1=1 |  |  |  | DataStorage 4 int16 | 47.24 | 1=1 |  |  |  | Process PID setpoint actual | 40.03 | 1=1unit | 100=1unit |  |  |  |  | Process PID output actual | 40.01 | 1=1% | FW Manual
[21 empty] | Limit to limit control status | 76.01 | 1=1 |  |  |  | Limit to limit control status | 76.01 | 1=1 |  |  |  | PFC status | 76.01 | 1=1 |  |  |  | Process PID status word | 40.06 | 1=1 | 1=1 |  |  |  |  | Process PID feedback actual | 40.02 | 1=1unit | FW Manual
[21 empty] | Motor Position | 90.02 | 32767=1rev |  |  |  | Motor Position | 90.02 | 32767=1rev |  |  |  | Multipump system status | 76.02 | 1=1 |  |  |  | Braking resistor temperature | 43.01 | 1=1% | 10=1% |  |  |  |  | Process PID setpoint actual | 40.03 | 1=1unit | FW Manual
[21 empty] | Encoder 1 position | 90.11 | 32767=1rev |  |  |  | Encoder 1 position | 90.11 | 32767=1rev |  |  |  | Pump status 1 | 76.11 | 1=1 |  |  |  | Brake control status | 44.01 | 1=1 | 1=1 |  |  |  |  | Process PID status word | 40.06 | 1=1 | FW Manual
[21 empty] | Encoder 1 revol extension | 90.13 | 1=1rev |  |  |  | Encoder 1 revol extension | 90.13 | 1=1rev |  |  |  | Pump status 2 | 76.12 | 1=1 |  |  |  | DataStorage 1 int32 | 47.11 | 1=1 | 1=1 |  |  |  |  | Brake control status | 44.01 | 1=1 | FW Manual
[21 empty] | Last ID run performed | 99.14 | 1=1 |  |  |  | Last ID run performed | 99.14 | 1=1 |  |  |  | Pump status 3 | 76.13 | 1=1 |  |  |  | DataStorage 2 int32 | 47.12 | 1=1 | 1=1 |  |  |  |  | M1 spd scaling act | 46.02 | 1=1rpm | FW Manual
[33 empty] | Pump status 4 | 76.14 | 1=1 |  |  |  | DataStorage 3 int32 | 47.13 | 1=1 | 1=1 |  |  |  |  | M1 torq scaling act | 46.04 | 100=1% | FW Manual
[33 empty] | Pump/fan 1 run time | 77.11 | 1=1h |  |  |  | DataStorage 4 int32 | 47.14 | 1=1 | 1=1 |  |  |  |  | DataStorage 1 int32 | 47.11 | 1=1 | FW Manual
[33 empty] | Pump/fan 2 run time | 77.12 | 1=1h |  |  |  | DataStorage 1 int16 | 47.21 | 1=1 | 1=1 |  |  |  |  | DataStorage 2 int32 | 47.12 | 1=1 | FW Manual
[33 empty] | Pump/fan 3 run time | 77.13 | 1=1h |  |  |  | DataStorage 2 int16 | 47.22 | 1=1 | 1=1 |  |  |  |  | DataStorage 3 int32 | 47.13 | 1=1 | FW Manual
[33 empty] | Pump/fan 4 run time | 77.14 | 1=1h |  |  |  | DataStorage 3 int16 | 47.23 | 1=1 | 1=1 |  |  |  |  | DataStorage 4 int32 | 47.14 | 1=1 | FW Manual
[33 empty] | Last ID run performed | 99.14 | 1=1 |  |  |  | DataStorage 4 int16 | 47.24 | 1=1 | 1=1 |  |  |  |  | DataStorage 1 int16 | 47.21 | 1=1 | FW Manual
[39 empty] | Motor Position | 90.02 | 32767=1rev | 100000000=1rev |  |  |  |  | DataStorage 2 int16 | 47.22 | 1=1 | FW Manual
[39 empty] | Encoder 1 position | 90.11 | 32767=1rev | 100000000=1rev |  |  |  |  | DataStorage 3 int16 | 47.23 | 1=1 | FW Manual
[39 empty] | Encoder 1 revol extension | 90.13 | 1=1rev | 1=1rev |  |  |  |  | DataStorage 4 int16 | 47.24 | 1=1 | FW Manual
[39 empty] | Actual checksum | 96.53 | 1=1 | 1=1 |  |  |  |  | Motor Position | 90.02 | 32767=1rev | FW Manual
[39 empty] | Last ID run performed | 99.14 | 1=1 | 1=1 |  |  |  |  | Load Position scaled | 90.05 | 1=1 | FW Manual
[47 empty] | Motor Position scaled | 90.06 | 1=1 | FW Manual
[47 empty] | Load pos scaled int | 90.07 | 1=1 | FW Manual
[21 empty] | ACS380 | [5 empty] | ACS480 | [5 empty] | ACS580 | [5 empty] | ACS880 | [7 empty] | DCS880
[21 empty] | Input Signal # |  |  | Output Signal # |  |  | Input Signal # |  |  | Output Signal # |  |  | Input Signal # |  |  | Output Signal # |  |  | Input Signal # |  | In Scaling16or32 |  | Output Signal # |  | Out Scaling16or32 |  | Input Signal # |  | In Scaling16or32 |  | Output Signal # |  | Out Scaling16or32
[21 empty] | 52.01= | #REF! | #REF! | 53.01= | #REF! | #REF! | 52.01= | #REF! | #REF! | 53.01= | #REF! | #REF! | 52.01= | #REF! | #REF! | 53.01= | #REF! | #REF! | 52.01= | #REF! | #REF! |  | 53.01= | #REF! | #REF! |  | 52.01= | #REF! | #REF! |  | 53.01= | #REF! | #REF!
[21 empty] | 52.02= | #REF! | #REF! | 53.02= | #REF! | #REF! | 52.02= | #REF! | #REF! | 53.02= | #REF! | #REF! | 52.02= | #REF! | #REF! | 53.02= | #REF! | #REF! | 52.02= | #REF! | #REF! |  | 53.02= | #REF! | #REF! |  | 52.02= | #REF! | #REF! |  | 53.02= | #REF! | #REF!
[21 empty] | 52.03= | #REF! | #REF! | 53.03= | #REF! | #REF! | 52.03= | #REF! | #REF! | 53.03= | #REF! | #REF! | 52.03= | #REF! | #REF! | 53.03= | #REF! | #REF! | 52.03= | #REF! | #REF! |  | 53.03= | #REF! | #REF! |  | 52.03= | #REF! | #REF! |  | 53.03= | #REF! | #REF!
[21 empty] | 52.04= | #REF! | #REF! | 53.04= | #REF! | #REF! | 52.04= | #REF! | #REF! | 53.04= | #REF! | #REF! | 52.04= | #REF! | #REF! | 53.04= | #REF! | #REF! | 52.04= | #REF! | #REF! |  | 53.04= | #REF! | #REF! |  | 52.04= | #REF! | #REF! |  | 53.04= | #REF! | #REF!
[21 empty] | 52.05= | #REF! | #REF! | 53.05= | #REF! | #REF! | 52.05= | #REF! | #REF! | 53.05= | #REF! | #REF! | 52.05= | #REF! | #REF! | 53.05= | #REF! | #REF! | 52.05= | #REF! | #REF! |  | 53.05= | #REF! | #REF! |  | 52.05= | #REF! | #REF! |  | 53.05= | #REF! | #REF!
[21 empty] | 52.06= | #REF! | #REF! | 53.06= | #REF! | #REF! | 52.06= | #REF! | #REF! | 53.06= | #REF! | #REF! | 52.06= | #REF! | #REF! | 53.06= | #REF! | #REF! | 52.06= | #REF! | #REF! |  | 53.06= | #REF! | #REF! |  | 52.06= | #REF! | #REF! |  | 53.06= | #REF! | #REF!
[21 empty] | 52.07= | #REF! | #REF! | 53.07= | #REF! | #REF! | 52.07= | #REF! | #REF! | 53.07= | #REF! | #REF! | 52.07= | #REF! | #REF! | 53.07= | #REF! | #REF! | 52.07= | #REF! | #REF! |  | 53.07= | #REF! | #REF! |  | 52.07= | #REF! | #REF! |  | 53.07= | #REF! | #REF!
[21 empty] | 52.08= | #REF! | #REF! | 53.08= | #REF! | #REF! | 52.08= | #REF! | #REF! | 53.08= | #REF! | #REF! | 52.08= | #REF! | #REF! | 53.08= | #REF! | #REF! | 52.08= | #REF! | #REF! |  | 53.08= | #REF! | #REF! |  | 52.08= | #REF! | #REF! |  | 53.08= | #REF! | #REF!
[21 empty] | 52.09= | #REF! | #REF! | 53.09= | #REF! | #REF! | 52.09= | #REF! | #REF! | 53.09= | #REF! | #REF! | 52.09= | #REF! | #REF! | 53.09= | #REF! | #REF! | 52.09= | #REF! | #REF! |  | 53.09= | #REF! | #REF! |  | 52.09= | #REF! | #REF! |  | 53.09= | #REF! | #REF!
[21 empty] | 52.10= | #REF! | #REF! | 53.10= | #REF! | #REF! | 52.10= | #REF! | #REF! | 53.10= | #REF! | #REF! | 52.10= | #REF! | #REF! | 53.10= | #REF! | #REF! | 52.10= | #REF! | #REF! |  | 53.10= | #REF! | #REF! |  | 52.10= | #REF! | #REF! |  | 53.10= | #REF! | #REF!
[22 empty] | Below are the Inputs and Outputs based on the selected VFD in cell I9 | [18 empty] | 3
[21 empty] | Inputs |  | Scaling |  |  |  | Outputs |  | Scaling
[21 empty] | Input 1 | #REF! | #REF! |  |  |  | Output 1 | #REF! | #REF!
[21 empty] | Input 2 | #REF! | #REF! |  |  |  | Output 2 | #REF! | #REF!
[21 empty] | Input 3 | #REF! | #REF! |  |  |  | Output 3 | #REF! | #REF!
[21 empty] | Input 4 | #REF! | #REF! |  |  |  | Output 4 | #REF! | #REF!
[21 empty] | Input 5 | #REF! | #REF! |  |  |  | Output 5 | #REF! | #REF!
[21 empty] | Input 6 | #REF! | #REF! |  |  |  | Output 6 | #REF! | #REF!
[21 empty] | Input 7 | #REF! | #REF! |  |  |  | Output 7 | #REF! | #REF!
[21 empty] | Input 8 | #REF! | #REF! |  |  |  | Output 8 | #REF! | #REF!
[21 empty] | Input 9 | #REF! | #REF! |  |  |  | Output 9 | #REF! | #REF!
[21 empty] | Input 10 | #REF! | #REF! |  |  |  | Output 10 | #REF! | #REF!
[28 empty] | input # | input param conversion |  | Output # | output param conversion
[20 empty] | Rockwell Parameter Name | Input Parameters | Input Scaling | 755 Output Parameter Name | Output Parameters | Output scaling |  |  | input 1 | 1.11 |  | output 1 | #N/A
[15 empty] | IF('Profile Selection'!$P$9="Scalar (V/Hz)",28.72,23.12) |  |  |  | 755 | Output Frequency | 1.06 | 100=1Hz | Accel Time 1 | 23.12 | 10=1s |  |  | input 2 | 1.07 |  | output 2 | #N/A
[20 empty] | Commanded SpdRef | 3.05 | 100=1rpm | Accel Time 2 | 23.13 | 10=1s |  |  | input 3 | #N/A |  | output 3 | #N/A
[15 empty] | IF($F$17="Powerflex525",$Y$225:$Y$235,$Y$207:$Y220) |  |  |  |  | Mtr Vel Fdbk | 1.01 | None | Decel Time 1 | 23.13 | 10=1s |  |  | input 4 | #N/A |  | output 4 | #N/A
[20 empty] | Output Current | 1.07 | 100=1A | Decel Time 2 | 23.15 | 10=1s |  |  | input 5 | #N/A |  | output 5 | #N/A
[20 empty] | Output Voltage | 1.13 | 1=1V | Preset Speed 1 | 22.26 | 100=1rpm |  |  | input 6 | #N/A |  | output 6 | #N/A
[20 empty] | Output Power | 1.14 | 100=1unit | Preset Speed 2 | 22.27 | 100=1rpm |  |  | input 7 | #N/A |  | output 7 | #N/A
[20 empty] | Elapsed kWH | 1.2 | 1=1kWh | Preset Speed 3 | 22.28 | 100=1rpm |  |  | input 8 | #N/A |  | output 8 | #N/A
[20 empty] | Elapsed mWH | 1.19 | 1=1MWh | Preset Speed 4 | 22.29 | 100=1rpm |  |  | input 9 | #N/A |  | output 9 | #N/A
[20 empty] | Elapsed Run Time | 5.02 | 1=1d | Preset Speed 5 | 22.3 | 100=1rpm |  |  | input 10 | #N/A |  | output 10 | #N/A
[20 empty] | Motor NP Volts | 99.07 | 10=1V | Preset Speed 6 | 22.31 | 100=1rpm
[20 empty] | Motor NP Amps | 99.06 | 1=1A | Preset Speed 7 | 22.32 | 100=1rpm
[20 empty] | Motor NP Hertz | 99.08 | 10=1Hz | Jog Speed 1 | 20.26 | 1=1
[20 empty] | Motor NP RPM | 99.09 | 1=1rpm | Jog Speed 2 | 20.27 | 1=1
[20 empty] | Digital In Sts | 10.01 | 1=1 | Jog Acc Dec Time | 23.20/23.21 | 10=1s
[20 empty] | Drive Temp C. | 5.11 | 1=1%
[20 empty] | Maximum Frequency | 30.14 | 1=1Hz
[20 empty] | DC Bus Volts | 1.11 | 1=1V
[20 empty] | Rockwell Parameters | Input Parameters | Input Scaling | 525 Output Parameter Name | Output Parameters | Output scaling
[19 empty] | 525 | Output Freq | 1.06 | 100=1Hz | Accel Time 1 | 23.12 | 10=1s
[20 empty] | Commanded Freq | 3.05 | 100=1Hz | Decel Time 1 | 23.13 | 10=1s
[20 empty] | Output Current | 1.07 | 100=1A | Preset Freq 1 | 22.26 | 100=1rpm
[20 empty] | Output Voltage | 1.13 | 1=1V | Preset Freq 2 | 22.27 | 100=1rpm
[20 empty] | DC Bus Voltage | 1.11 | 1=1V | Preset Freq 3 | 22.28 | 100=1rpm
[20 empty] | Drive Status | 6.16/6.17 | 1=1 | Preset Freq 4 | 22.29 | 100=1rpm
[20 empty] | Fault 1 Code | 4.01 | 1=1 | Preset Freq 5 | 22.3 | 100=1rpm
[20 empty] | Fault 2 Code | 4.02 | 1=1 | Preset Freq 6 | 22.31 | 100=1rpm
[20 empty] | Fault 3 Code | 4.03 | 1=1 | Preset Freq 45454 | 22.32 | 100=1rpm
[20 empty] | Control Source | 20.11 | 1=1 | Jog Frequency | 22.42 | 100=1rpm
[20 empty] | Dig In Status | 10.01 | 1=1 | Jog Accel/Decel | 23.20/23.21 | 10=1s
[20 empty] | Output Speed | 1.01 | 100=1rpm
[20 empty] | Output Power | 1.14 | 100=1kWh
[20 empty] | Elapsed Run Time | 5.02 | 1=1d
[20 empty] | Elapsed kWH | 1.2 | 10=1kWh
[20 empty] | Elapsed MWH | 1.33 | 1=1MWh
[20 empty] | Drive Temp | 5.11 | 1=1%
[20 empty] | Motor NP Volts | 99.07 | 10=1V
[20 empty] | Motor NP Hertz | 99.08 | 10=1Hz
[20 empty] | Motor NP RPM | 99.09 | 1=1rpm
[20 empty] | Motor NP Power | 99.1 | 1=1unit
[20 empty] | Minimum Freq | 30.13 | 1=1Hz
[20 empty] | Maximum Freq | 30.14 | 1=1Hz
[23 empty] | output table for dropdown** | Output Scaling
[23 empty] | Accel Time 1 | 10=1s
[23 empty] | Accel Time 2 | 10=1s
[23 empty] | Decel Time 1 | 10=1s
[23 empty] | Decel Time 2 | 10=1s
[23 empty] | Preset Speed 1 | 100=1rpm
[23 empty] | Preset Speed 2 | 100=1rpm
[23 empty] | Preset Speed 3 | 100=1rpm
[23 empty] | Preset Speed 4 | 100=1rpm
[23 empty] | Preset Speed 5 | 100=1rpm
[23 empty] | Preset Speed 6 | 100=1rpm
[23 empty] | Preset Speed 7 | 100=1rpm
[23 empty] | Preset Freq 1 | 100=1rpm
[23 empty] | Preset Freq 2 | 100=1rpm
[23 empty] | Preset Freq 3 | 100=1rpm
[23 empty] | Preset Freq 4 | 100=1rpm
[23 empty] | Preset Freq 5 | 100=1rpm
[23 empty] | Preset Freq 6 | 100=1rpm
[23 empty] | Preset Freq 7 | 100=1rpm
[23 empty] | Jog Speed 1 | 1=1
[23 empty] | Jog Speed 2 | 1=1
[23 empty] | Jog Accel/Decel | 10=1s
[23 empty] | Jog Frequency | 100=1rpm
Revision A
ABBDrives
Note on P9: ACS380,ACS480, ACx580 support both Vector and Scalar mode in parameter 99.04. Vector improves speed control accuracy with changing loads and reference is controlled in RPM. Scalar is a V/Hz simplified control with the speed reference in Hz. ACS880 supports DTC which is a High Performance Sensorless Vector or Closed Loop Vector control mode with Speed Reference controlled in RPM. Again a simplified V/Hz control mode can be selected with Scalar in ACS880, speed reference can be controlled in RPM or Hz. The Control mode is also defined in parameter 99.04 in the ACS880. DCS880 should have Control Mode set to Speed, but Torque control can also be selected with Step 3 below.
Note on D21: Instructions: Select signal from drop down list, or manually over write with an actual Parameter # (Required Parameter form is: Group#.Index#, ie 1.07) Data Information: Excluding the Status Word, Actual Speed, and Actual Torque define the 1st User Data Word Sent from the VFD back to the PLC . This parameter will be configured in 52.01 (FBA data in 1)
Note on J21: Instructions: Select signal from drop down list, or manually over write with an actual Parameter # (Required Parameter form is: Group#.Index#, ie 10.23) Data Information: Excluding the Control Word, Speed Reference, and Reference 2, define the 1st User Data Word sent from the PLC to the VFD This parameter will be configured in 53.01 (FBA data out 1)
Note on R21: Steve Boren: The Status Word is comprised of multiple status bits consisting of signals like: Ready, Running, Faulted, Warning active. In some profiles other bits may also be present such as VFD Enabled, VFD At Speed, VFD in Local or Remote Mode, VFD EXT1 or EXT2 Control Mode, what run permissive may have been used to issue a Stop command, VFD is operating in a Limit Condition, etc.
Note on U21: Steve Boren: The Control Word will consist of multiple control bits such as: Run/Stop Command, Fault Reset, and in some profiles also the Direction Command, Enable Command, Reference Selection Bit, various bits to control the Reference Ramp Generator, and various Stopping Internock Bits. This is always the first word of the communicated Data sent as an Output from the PLC to the VFD
Note on D22: Instructions: Select signal from drop down list, or manually over write with an actual Parameter # (Required Parameter form is: Group#.Index#, ie 1.07) Data Information: Excluding the Status Word, Actual Speed, and Actual Torque define the 1st User Data Word Sent from the VFD back to the PLC . This parameter will be configured in 52.02 (FBA data in 2)
Note on J22: Instructions: Select signal from drop down list, or manually over write with an actual Parameter # (Required Parameter form is: Group#.Index#, ie 10.23) Data Information: Excluding the Control Word, Speed Reference, and Reference 2, define the 1st User Data Word sent from the PLC to the VFD This parameter will be configured in 53.02 (FBA data out 2)
Note on R22: Steve Boren: Actual Speed will always be the Second word sent from the VFD to the PLC as an Input. In some profiles, Bit 15 will be a Sign Bit for direction indication.
Note on U22: Steve Boren: The speed reference will always be the second data word sent as an output from the PLC to the VFD. The scaling of the speed reference will depend upon the Profile utilized. In some profiles, Bit 15 is used as a Sign Bit for Direction
Note on D23: Instructions: Select signal from drop down list, or manually over write with an actual Parameter # (Required Parameter form is: Group#.Index#, ie 1.07) Data Information: Excluding the Status Word, Actual Speed, and Actual Torque define the 1st User Data Word Sent from the VFD back to the PLC . This parameter will be configured in 52.03 (FBA data in 3)
Note on J23: Instructions: Select signal from drop down list, or manually over write with an actual Parameter # (Required Parameter form is: Group#.Index#, ie 10.23) Data Information: Excluding the Control Word, Speed Reference, and Reference 2, define the 1st User Data Word sent from the PLC to the VFD This parameter will be configured in 53.03 (FBA data out 3)
Note on D24: Instructions: Select signal from drop down list, or manually over write with an actual Parameter # (Required Parameter form is: Group#.Index#, ie 1.07) Data Information: Excluding the Status Word, Actual Speed, and Actual Torque define the 1st User Data Word Sent from the VFD back to the PLC . This parameter will be configured in 52.04 (FBA data in 14
Note on J24: Instructions: Select signal from drop down list, or manually over write with an actual Parameter # (Required Parameter form is: Group#.Index#, ie 10.23) Data Information: Excluding the Control Word, Speed Reference, and Reference 2, define the 1st User Data Word sent from the PLC to the VFD This parameter will be configured in 53.04 (FBA data out 4)
Note on D25: Instructions: Select signal from drop down list, or manually over write with an actual Parameter # (Required Parameter form is: Group#.Index#, ie 1.07) Data Information: Excluding the Status Word, Actual Speed, and Actual Torque define the 1st User Data Word Sent from the VFD back to the PLC . This parameter will be configured in 52.05 (FBA data in 5)
Note on J25: Instructions: Select signal from drop down list, or manually over write with an actual Parameter # (Required Parameter form is: Group#.Index#, ie 10.23) Data Information: Excluding the Control Word, Speed Reference, and Reference 2, define the 1st User Data Word sent from the PLC to the VFD This parameter will be configured in 53.05 (FBA data out 5)
Note on D26: Instructions: Select signal from drop down list, or manually over write with an actual Parameter # (Required Parameter form is: Group#.Index#, ie 1.07) Data Information: Excluding the Status Word, Actual Speed, and Actual Torque define the 1st User Data Word Sent from the VFD back to the PLC . This parameter will be configured in 52.06 (FBA data in 6)
Note on J26: Instructions: Select signal from drop down list, or manually over write with an actual Parameter # (Required Parameter form is: Group#.Index#, ie 10.23) Data Information: Excluding the Control Word, Speed Reference, and Reference 2, define the 1st User Data Word sent from the PLC to the VFD This parameter will be configured in 53.06 (FBA data out 6)
Note on D27: Instructions: Select signal from drop down list, or manually over write with an actual Parameter # (Required Parameter form is: Group#.Index#, ie 1.07) Data Information: Excluding the Status Word, Actual Speed, and Actual Torque define the 1st User Data Word Sent from the VFD back to the PLC . This parameter will be configured in 52.07 (FBA data in 7)
Note on J27: Instructions: Select signal from drop down list, or manually over write with an actual Parameter # (Required Parameter form is: Group#.Index#, ie 10.23) Data Information: Excluding the Control Word, Speed Reference, and Reference 2, define the 1st User Data Word sent from the PLC to the VFD This parameter will be configured in 53.07 (FBA data out 7)
Note on D28: Instructions: Select signal from drop down list, or manually over write with an actual Parameter # (Required Parameter form is: Group#.Index#, ie 1.07) Data Information: Excluding the Status Word, Actual Speed, and Actual Torque define the 1st User Data Word Sent from the VFD back to the PLC . This parameter will be configured in 52.08 (FBA data in 8)
Note on J28: Instructions: Select signal from drop down list, or manually over write with an actual Parameter # (Required Parameter form is: Group#.Index#, ie 10.23) Data Information: Excluding the Control Word, Speed Reference, and Reference 2, define the 1st User Data Word sent from the PLC to the VFD This parameter will be configured in 53.08 (FBA data out 8)
Note on D29: Instructions: Select signal from drop down list, or manually over write with an actual Parameter # (Required Parameter form is: Group#.Index#, ie 1.07) Data Information: Excluding the Status Word, Actual Speed, and Actual Torque define the 1st User Data Word Sent from the VFD back to the PLC . This parameter will be configured in 52.09 (FBA data in 9)
Note on J29: Instructions: Select signal from drop down list, or manually over write with an actual Parameter # (Required Parameter form is: Group#.Index#, ie 10.23) Data Information: Excluding the Control Word, Speed Reference, and Reference 2, define the 1st User Data Word sent from the PLC to the VFD This parameter will be configured in 53.09 (FBA data out 9)
Note on D30: Instructions: Select signal from drop down list, or manually over write with an actual Parameter # (Required Parameter form is: Group#.Index#, ie 1.07) Data Information: Excluding the Status Word, Actual Speed, and Actual Torque define the 1st User Data Word Sent from the VFD back to the PLC . This parameter will be configured in 52.10 (FBA data in 10)
Note on J30: Instructions: Select signal from drop down list, or manually over write with an actual Parameter # (Required Parameter form is: Group#.Index#, ie 10.23) Data Information: Excluding the Control Word, Speed Reference, and Reference 2, define the 1st User Data Word sent from the PLC to the VFD This parameter will be configured in 53.10 (FBA data out 10)
Note on F41: Define the 1st octet of the IP address of the VFD
Note on G41: Define the 2nd octet of the IP address of the VFD
Note on H41: Define the 3rd octet of the IP address of the VFD
Note on I41: Define the 4th octet of the IP address of the VFD

## ODVA ACDC Basic Profile (hidden)
Ethernet IP ODVA AC/DC Drive Basic Profile |  |  |  | FENA-11/21 Configuration Parameters (Group 50 & 51)
|  |  |  | Parameter Name | Parameter | Parameter Setting |  | Rockwell Logix 5000 Software Configuration to add ABB VFDs as a new Ethernet IP Device
VFD Signals Controlled by PLC over EIP |  |  |  | FBA A enable | 50.01 | Please Select.. |  | Note: The configuration below is specific to the ODVA AC/DC Profile and the data
Signal | No/Yes | Parameter | Parameter Setting | FBA A comm loss func | 50.02 | Fault |  | supplied on the "Profile Selection" Tab of this Spreadsheet Tool. This PLC configuration
Run Command | YES | 20.01 | Fieldbus A | FBA ref1 type | 50.04 | Auto |  | matches the parameters defined on this page and will deliver successful Communications
Fault Reset | YES | 31.11 | "No Setting Required" | FBA ref2 type | 50.05 | Auto |  | between the PLC and the ABB VFD via Ethernet IP
Speed Reference | YES | 22.11 | FB A ref1 | FBA actual 1 type | 50.07 | Auto
Torque Reference | NO | 26.11 | "User Defines Setting" | FBA actual 2 type | 50.08 | Torque
Parameters for Configuring User Defined Data Words |  |  |  | FBA A Type | 51.01 | Ethernet
Inputs (Read) to PLC from VFD |  | Outputs (Write) from PLC to VFD |  | Protocol / Profile | 51.02 | 100 (EIP AC/DC)
Parameter | Parameter Setting | Parameter | Parameter Setting | IP configuration | 51.04 | 0 (Static)
52.01 (16bit) | NA | 53.01 (16bit) | NA | IP Address 1 | 51.05 | 192
52.02 (16bit) | NA | 53.02 (16bit) | NA | IP Address 2 | 51.06 | 168
52.03 (16bit) | NA | 53.03 (16bit) | NA | IP Address 3 | 51.07 | 3 | [7 empty] | NA | NA
52.04 (16bit) | NA | 53.04 (16bit) | NA | IP Address 4 | 51.08 | 3 | [7 empty] | NA | NA
52.05 (16bit) | NA | 53.05 (16bit) | NA | Subnet CIDR | 51.09 | 24 | [7 empty] | 1 | 0
52.06 (16bit) | NA | 53.06 (16bit) | NA | GW Address 1 | 51.1 | 0 |  |  |  | 192 | 168 | 3 | 3
52.07 (16bit) | NA | 53.07 (16bit) | NA | GW Address 2 | 51.11 | 0
52.08 (16bit) | NA | 53.08 (16bit) | NA | GW Address 3 | 51.12 | 0
52.09 (16bit) | NA | 53.09 (16bit) | NA | GW Address 4 | 51.13 | 0
52.10 (16bit) | NA | 53.10 (16bit) | NA | Control Timeout | 51.2 | 20
|  |  |  | Idle Action | 51.21 | 0 (Off-line)
|  |  |  | ODVA Stop Function | 51.22 | Ramp
|  |  |  | ODVA Speed Scale | 51.23 | 128 |  | ODVA Basic Control Word Bit Structure
|  |  |  | ODVA Torque Scale | 51.24 | 128
|  |  |  | FBA Par Refresh | 51.27 | Configure
|  |  |  | Other VFD Parameters that Accompany Communication Control |  |  |  | ODVA Basic Status Word Bit Structure
|  |  |  | Parameter Name | Parameter | Parameter Setting | Units
|  |  |  | Acceleration Time 1 | 23.12 | 5 | s
|  |  |  | Deceleration Time 1 | 23.13 | 5 | s
|  |  |  | Minimum Speed | 30.11 | 0 | rpm
|  |  |  | Maximum Speed | 30.12 | 1800 | rpm
|  |  |  | Speed Scaling | 46.01 | 1800 | rpm
[7 empty] | Output | Input | Size
[7 empty] | NA | NA | NA
ACH580
2
Assembly Instances for ODVA ACDC Basic Profile
|  | AC settings | DCS880 settings |  |  |  | Output | Input | Size
| NO | "User Defines Setting" | Local I/O |  |  |  | NA | NA | NA
| YES | Fieldbus A | Main control word |  |  |  | 20 | 70 | 2
| NO | "User Defines Setting" | "User Defines Setting" |  |  |  | 22 | 72 | 3
| YES | "No Setting Required" | "No Setting Required" |  |  |  | 120 | 170 | 12
| NO | "User Defines Setting" | "User Defines Setting" |  |  |  | 122 | 172 | 13
| YES | FB A ref1 | FBA A ref1
| NO | "User Defines Setting" | "User Defines Setting"
| YES | FB A ref2 | FBA A ref2
ABB VFD
ABB All-Compatible VFD
ODVA ACDC Basic Profile
Data - INT
Note on H3: If the drive being used is ACS880 or DCS880, then define the option slot which the Ethernet IP module is mounted. Otherwise, if drive being used is ACS380, ACS480, ACx580 then select "Enable" as Ethernet IP module can only be mounted in one location on the VFD and it must be turned on.
Note on H4: Once this parameter is set to Fault, the ABB Drive will enter into a faulted state until PLC comms are established, at that time the fault can be reset. Refer to the resprective ABB Drive Firmware Manual for a description of each setting available.
Note on D6: Parameter 31.11 is the Fault Reset Selection parameter, but it is not needed when ODVA AC/DC Profile is used as the Fault Reset bit is internal connected in the software of the VFD.
Note on H7: This configuraiton tool automatically defines the proper setting for this parameter based on other selections in the tool. Note: If Speed Reference 1 (parameter 22.11) is not being controlled via communications, then set cell B7=NO (Speed Reference Control) to the left to represent this actual setup, which will then automatically configure this parameter. If 22.11= AI1 scaled for example, this parameter must be set to "Speed" to properly scale the speed feedback to the PLC.
Note on H8: This configuraiton tool automatically defines the proper setting for this parameter based on other selections in the tool. Note: If Torque Reference 1 (parameter 26.11) is not being controlled via communications, then set cell B8=NO (Torque Reference Control) to the left to represent this actual setup, which will then automatically configure this parameter. If parameter 26.11= AI1 scaled for example, then this parameter must be set to "Torque" to properly scale Torque Feedback to the PLC if the profile utilized has torque included (This is taken into account by selecting "YES" in Step 3 of the "Profile Selection" tab.)
Note on H10: This parameter is read only, and should simply be checked to make sure "Ethernet" or "Ethernet/IP" is displayed which signifies that the FENA or FEIP module (respectively) is recognized by the VFD
Note on H11: This parameter configures the VFD for ODVA ACDC Drive Basic Profile, this setting is used in conjunction with the Rockwell EIP Module Config screen shown to the right to establish comms between PLC and the ABB VFD.
Note on H17: The FENA user manual has a table description of different formats for the Subnet Mask and the associated CIDR setting. 24 = 255.255.255.0
Note on H18: First Octet address for utilizing comms via a gateway from another network
Note on H19: Second Octet address for utilizing comms via a gateway from another network
Note on H20: Third Octet address for utilizing comms via a gateway from another network
Note on H21: Forth Octet address for utilizing comms via a gateway from another network
Note on H22: The actual Timeout time is 100ms x Control Timeout Setting. This is the time in which the FENA or FEIP module will stop sending data to the ABB Drive to signal comm loss. Comm Loss Function (50.02) and Comm Loss timeout (50.03) define what the ABB Drive will do when it stops receiving comms from the Ethernet IP Module.
Note on H23: This parameter defines the action of the Ethernet module takes when a Network Idle State is determined. Off-line will halt comms with the drive, and the Drive Comm Loss function (parameter 50.02) determines the actioin the drive will take. Value of 1 means Online, so module will continue to transfer the last data to the VFD when Network is Idle
Note on H24: This parameter defines the type of Stopping Function that VFD will use when the Run bit in the Control Word is removed
Note on H25: This parameter defines the speed scaling used for the Speed Reference and Actual speed when ODVA AC/DC drive profile is used. Value of 128 shown on the VFD keypad means that speed is scaled 1 = 1rpm
Note on H26: This parameter defines the torque scaling used for the Torque Reference and Actual Torque when ODVA AC/DC drive profile is used. Value of 128 shown on the VFD keypad means that Torque is scaled 1 = 1N-m
Note on H27: Parameter Refresh must be triggered after any changes are made to parameters in Group 50, 51, 52, 53 before they take effect and become active
Note on H34: This parameter should be set the same as the Maximum desired operation Speed or Frequency in the Reverse Rotation. Because ODVA Basic Profile does not support direction, this parameter can be set to 0 rpm or Hz.
Note on H35: This parameter should be set the same as the Maximum desired operation Speed or Frequency.
Note on H36: This parameter should be set the same as the Maximum desired operation Speed or Frequency.

## ODVA ACDC Extended Profile (hidden)
EIP ODVA AC/DC Drive Extended Profile |  |  |  | FENA-11/21 Configuration Parameters (Group 50 & 51)
|  |  |  | Parameter Name | Parameter | Parameter Setting |  | Rockwell Logix 5000 Software Configuration to add ABB VFDs as a new Ethernet IP Device
VFD Signals Controlled by PLC over EIP |  |  |  | FBA A enable | 50.01 | Please Select.. |  | Note: The configuration below is specific to the ODVA AC/DC Extended Profile and the data
Signal | No/Yes | Parameter | Parameter Setting | FBA A comm loss func | 50.02 | Fault |  | supplied on the "Profile Selection" Tab of this Spreadsheet Tool. This PLC configuration
Run Command | YES | 20.01 | Fieldbus A | FBA ref1 type | 50.04 | Auto |  | matches the parameters defined on this page and will deliver successful Communications
Fault Reset | YES | 31.11 | "No Setting Required" | FBA ref2 type | 50.05 | Auto |  | between the PLC and the ABB VFD via Ethernet IP
Speed Reference | YES | 22.11 | FB A ref1 | FBA actual 1 type | 50.07 | Auto
Direction Command | YES | 20.21 | Request | FBA actual 2 type | 50.08 | Torque
Torque Reference | NO | 26.11 | "User Defines Setting"
|  |  |  | FBA A Type | 51.01 | Ethernet
Parameters for Configuring User Defined Data Words |  |  |  | Protocol / Profile | 51.02 | 100 (EIP AC/DC)
Inputs (Read) to PLC from VFD |  | Outputs (Write) from PLC to VFD |  | IP configuration | 51.04 | 0 (Static)
Parameter | Parameter Setting | Parameter | Parameter Setting | IP Address 1 | 51.05 | 192
52.01 (16bit) | NA | 53.01 (16bit) | NA | IP Address 2 | 51.06 | 168
52.02 (16bit) | NA | 53.02 (16bit) | NA | IP Address 3 | 51.07 | 3 | [7 empty] | NA | NA
52.03 (16bit) | NA | 53.03 (16bit) | NA | IP Address 4 | 51.08 | 3 | [7 empty] | NA | NA
52.04 (16bit) | NA | 53.04 (16bit) | NA | Subnet CIDR | 51.09 | 24 | [7 empty] | 1 | 0
52.05 (16bit) | NA | 53.05 (16bit) | NA | GW Address 1 | 51.1 | 0 |  |  |  | 192 | 168 | 3 | 3
52.06 (16bit) | NA | 53.06 (16bit) | NA | GW Address 2 | 51.11 | 0
52.07 (16bit) | NA | 53.07 (16bit) | NA | GW Address 3 | 51.12 | 0
52.08 (16bit) | NA | 53.08 (16bit) | NA | GW Address 4 | 51.13 | 0
52.09 (16bit) | NA | 53.09 (16bit) | NA | Control Timeout | 51.2 | 20
52.10 (16bit) | NA | 53.10 (16bit) | NA | Idle Action | 51.21 | 0 (Off-line)
|  |  |  | ODVA Stop Function | 51.22 | Ramp
|  |  |  | ODVA Speed Scale | 51.23 | 128 |  | ODVA Extended Control Word Bit Structure
|  |  |  | ODVA Torque Scale | 51.24 | 128
|  |  |  | FBA Par Refresh | 51.27 | Configure
|  |  |  | Other VFD Parameters that Accompany Communication Control |  |  |  | ODVA Extended Status Word Bit Structure
|  |  |  | Parameter Name | Parameter | Parameter Setting | Units
|  |  |  | Acceleration Time 1 | 23.12 | 5.00 s | s
|  |  |  | Deceleration Time 1 | 23.13 | 5.00 s | s
|  |  |  | Minimum Speed | 30.11 | 0 | rpm
|  |  |  | Maximum Speed | 30.12 | 1800 | rpm
|  |  |  | Speed Scaling | 46.01 | 1800 | rpm
[7 empty] | Output | Input | Size
[7 empty] | NA | NA | NA
|  | 2 |  |  |  |  | Assembly Instances for ODVA ACDC Basic Profile
[7 empty] | Output | Input | Size
|  | AC Settings | DCS880 settings |  |  |  | NA | NA | NA
Run Cmd Selection | NO | "User Defines Setting" | Local I/O |  |  |  | 21 | 71 | 2
| YES | Fieldbus A | Main control word |  |  |  | 23 | 73 | 3
Fault Reset Selection | NO | "User Defines Setting" | "User Defines Setting" |  |  |  | 121 | 171 | 12
| YES | "No Setting Required" | "No Setting Required" |  |  |  | 123 | 173 | 13
Speed/Freq Ref Selection | NO | "User Defines Setting" | "User Defines Setting"
| YES | FB A ref1 | FBA A ref1
Torque Selection | NO | "User Defines Setting" | "User Defines Setting"
| YES | FB A ref2 | FBA A ref2
Direction Selection | NO | "User Defines Setting"
| YES | Request
ABB VFD
ABB All-Compatible VFD
ODVA ACDC Extended
Data - INT
Note on H3: If the drive being used is ACS880 or DCS880, then define the option slot which the Ethernet IP module is mounted. Otherwise, if drive being used is ACS380, ACS480, ACx580 then select "Enable" as Ethernet IP module can only be mounted in one location on the VFD and it must be turned on.
Note on H4: Once this parameter is set to Fault, the ABB Drive will enter into a faulted state until PLC comms are established, at that time the fault can be reset. Refer to the resprective ABB Drive Firmware Manual for a description of each setting available.
Note on D6: Parameter 31.11 is the Fault Reset Selection parameter, but it is not needed when ODVA AC/DC Profile is used as the Fault Reset bit is internal connected in the software of the VFD.
Note on H7: This configuraiton tool automatically defines the proper setting for this parameter based on other selections in the tool. Note: If Speed Reference 1 (parameter 22.11) is not being controlled via communications, then set cell B7=NO (Speed Reference Control) to the left to represent this actual setup, which will then automatically configure this parameter. If 22.11= AI1 scaled for example, this parameter must be set to "Speed" to properly scale the speed feedback to the PLC.
Note on H8: This configuraiton tool automatically defines the proper setting for this parameter based on other selections in the tool. Note: If Torque Reference 1 (parameter 26.11) is not being controlled via communications, then set cell B9=NO (Torque Reference Control) to the left to represent this actual setup, which will then automatically configure this parameter. If parameter 26.11= AI1 scaled for example, then this parameter must be set to "Torque" to properly scale Torque Feedback to the PLC if the profile utilized has torque included (This is taken into account by selecting "YES" in Step 3 of the "Profile Selection" tab.)
Note on H10: This parameter is read only, and should simply be checked to make sure "Ethernet" or "Ethernet/IP" is displayed which signifies that the FENA or FEIP module (respectively) is recognized by the VFD
Note on H11: This parameter configures the VFD for ODVA ACDC Drive Extended Profile, this setting is used in conjunction with the Rockwell EIP Module Config screen shown to the right to establish comms between PLC and the ABB VFD.
Note on H17: The FENA user manual has a table description of different formats for the Subnet Mask and the associated CIDR setting. 24 = 255.255.255.0
Note on H18: First Octet address for utilizing comms via a gateway from another network
Note on H19: Second Octet address for utilizing comms via a gateway from another network
Note on H20: Third Octet address for utilizing comms via a gateway from another network
Note on H21: Forth Octet address for utilizing comms via a gateway from another network
Note on H22: The actual Timeout time is 100ms x Control Timeout Setting. This is the time in which the FENA or FEIP module will stop sending data to the ABB Drive to signal comm loss. Comm Loss Function (50.02) and Comm Loss timeout (50.03) define what the ABB Drive will do when it stops receiving comms from the Ethernet IP Module.
Note on H23: This parameter defines the action of the Ethernet module takes when a Network Idle State is determined. Off-line will halt comms with the drive, and the Drive Comm Loss function (parameter 50.02) determines the actioin the drive will take. Value of 1 means Online, so module will continue to transfer the last data to the VFD when Network is Idle
Note on H24: This parameter defines the type of Stopping Function that VFD will use when the Run bit in the Control Word is removed
Note on H25: This parameter defines the speed scaling used for the Speed Reference and Actual speed when ODVA AC/DC drive profile is used. Value of 128 shown on the VFD keypad means that speed is scaled 1 = 1rpm
Note on H26: This parameter defines the torque scaling used for the Torque Reference and Actual Torque when ODVA AC/DC drive profile is used. Value of 128 shown on the VFD keypad means that Torque is scaled 1 = 1N-m
Note on H27: Parameter Refresh must be triggered after any changes are made to parameters in Group 50, 51, 52, 53 before they take effect and become active
Note on H34: This parameter should be set the same as the Maximum desired operation Speed or Frequency in the Reverse Rotation. Because ODVA Basic Profile does not support direction, this parameter can be set to 0 rpm or Hz.
Note on H35: This parameter should be set the same as the Maximum desired operation Speed or Frequency.
Note on H36: This parameter should be set the same as the Maximum desired operation Speed or Frequency.

## ABB Drives Setup
Ethernet IP ABB Drives Profile |  |  |  |  | FENA-11/21 Configuration Parameters (Group 50 & 51)
[5 empty] | Parameter Name | Parameter | Parameter Setting |  | Rockwell Logix 5000 Software Configuration to add ABB VFDs as a new Ethernet IP Device | [8 empty] | After the import of the Drive Emulation AOI be sure to label the proper data links on the new tags with the proper names associated with the data used.
VFD Signals Controlled by PLC over EIP |  |  |  |  | FBA A enable | 50.01 | Enable |  | Note: The configuration below is specific to the ABB Drives Profile and the data | [8 empty] | The Control word and speed reference as well as status word and speed feedback is already premapped. Any other data mapped will need to be labeled in the description field
Signal | No/Yes | Parameter | Parameter Setting |  | FBA A comm loss func | 50.02 | Fault |  | supplied on the "Profile Selection" Tab of this Spreadsheet Tool. This PLC configuration | [8 empty] | Copy and paste the description name from below into the description field of the tags generated from creating the AOI rung tags for the input and output data
EXT1/EXT2 Select | NO | 19.11 | EXT1 |  | FBA ref1 type | 50.04 | Auto |  | matches the parameters defined on this page and will deliver successful Communications
EXT1 Run Command | YES | 20.01 | Fieldbus A |  | FBA ref2 type | 50.05 | Auto |  | between the PLC and the ABB VFD via Ethernet IP
EXT2 Run Command | NO | 20.06 | "User Defines Setting" |  | FBA actual 1 type | 50.07 | Auto
Direction Command | YES | 20.21 | Request |  | FBA actual 2 type | 50.08 | Torque
Speed Reference 1 | YES | 22.11 | FB A ref1
Speed Reference 2 | NO | 22.18 | "User Defines Setting" |  | FBA A Type | 51.01 | Ethernet
Speed Ref 1/2 Sel | NO | See 19.11 | "See Ext1/Ext2 Sel" |  | Protocol / Profile | 51.02 | 101 (EIP ABB Pro)
Torque Reference 1 | NO | 26.11 | "User Defines Setting" |  | IP configuration | 51.04 | 0 (Static)
Fault Reset | YES | 31.11 | FBA A MCW bit 7 |  | IP Address 1 | 51.05 | 192
[5 empty] | IP Address 2 | 51.06 | 168
[5 empty] | IP Address 3 | 51.07 | 3 | [7 empty] | 152 | 13
Parameters for Configuring User Defined Data Words |  |  |  |  | IP Address 4 | 51.08 | 3 | [7 empty] | 102 | 13
Inputs (Read) to PLC from VFD |  | Outputs (Write) from PLC to VFD |  |  | Subnet CIDR | 51.09 | 24 | [7 empty] | 1 | 0
Parameter | Parameter Setting | Parameter | Parameter Setting |  | GW Address 1 | 51.1 | 0 |  |  |  | 192 | 168 | 3 | 3
52.01 (16bit) | 1.11 | 53.01 (16bit) | #N/A |  | GW Address 2 | 51.11 | 0
52.02 (16bit) | 1.07 | 53.02 (16bit) | #N/A |  | GW Address 3 | 51.12 | 0
52.03 (16bit) | #N/A | 53.03 (16bit) | #N/A |  | GW Address 4 | 51.13 | 0
52.04 (16bit) | #N/A | 53.04 (16bit) | #N/A |  | Control Timeout | 51.2 | 20
52.05 (16bit) | #N/A | 53.05 (16bit) | #N/A |  | Idle Action | 51.21 | 0 (Off-line)
52.06 (16bit) | #N/A | 53.06 (16bit) | #N/A |  | FBA Par Refresh | 51.27 | Configure
52.07 (16bit) | #N/A | 53.07 (16bit) | #N/A
52.08 (16bit) | #N/A | 53.08 (16bit) | #N/A | [15 empty] | DC Bus Volts
52.09 (16bit) | #N/A | 53.09 (16bit) | #N/A |  | Other VFD Parameters that Accompany Communication Control | [13 empty] | Output Current
52.10 (16bit) | #N/A | 53.10 (16bit) | #N/A |  | Parameter Name | Parameter | Parameter Setting | Units
[5 empty] | Acceleration Time 1 | 23.12 | 5.00 s | s
[5 empty] | Deceleration Time 1 | 23.13 | 5.00 s | s
[5 empty] | Minimum Speed | 30.11 | 0 | rpm
[5 empty] | Maximum Speed | 30.12 | 1800 | rpm
[5 empty] | Speed Scaling | 46.01 | 1800 | rpm
[5 empty] | Power Scaling | 46.04 | 1000 | N/A
[5 empty] | Current Scaling | 46.05 | 1000 | A
[8 empty] | Output | Input | Size | [6 empty] | DC Bus Volts
[8 empty] | 1 | 1 | 2 | [6 empty] | Output Current
|  | 2 | [5 empty] | Assembly Instances for ODVA ACDC Basic Profile
|  | AC Settings | DCS880 Settings |  |  |  |  | Output | Input | Size
Run Cmd Selection | NO | "User Defines Setting" | Local I/O |  |  |  |  | NA | NA | NA
| YES | Fieldbus A | Main control word |  |  |  |  | 1 | 51 | 2
Fault Reset Selection | NO | "User Defines Setting" | "User Defines Setting" |  |  |  |  | 2 | 52 | 3
| YES | FBA A MCW bit 7 | "No Setting Required" |  |  |  |  | 101 | 151 | 12
Spd/Freq Ref1 Selection | NO | "User Defines Setting" | "User Defines Setting" |  |  |  |  | 102 | 152 | 13
| YES | FB A ref1 | FBA A ref1
Direction Selection | NO | "User Defines Setting"
| YES | Request
EXT1/EXT2 Sel | NO | EXT1
| YES | FBA A MCW bit 11
Spd/Freq Ref2 Selecton | NO | "User Defines Setting" | "User Defines Setting"
| YES | FB A ref2 | FBA A ref2
Torque Selection | NO | "User Defines Setting" | "User Defines Setting"
| YES | FB A ref2 | FBA A ref2
Spd/Freq Ref1/2 Sel | NO
YES
| Ext1 Run Cmd Param | Flt Reset Param | Spd/Freq Ref1 Sel | NA | EXT1/EXT2 Sel | Spd/Freq Ref2 Sel | Ref 1/2 Selection | Torq Ref | Ext2 Run Cmd
ACS380 | 20.01 | 31.11 | 22.11 | NA | 19.11 | 22.18 | See 19.11 | 26.11 | 20.06
ACS480 | 20.01 | 31.11 | 22.11 | NA | 19.11 | 22.18 | See 19.11 | 26.11 | 20.06
ACS580 | 20.01 | 31.11 | 22.11 | NA | 19.11 | 22.18 | See 19.11 | 26.11 | 20.06
ACS880 | 20.01 | 31.11 | 22.11 | NA | 19.11 | 22.12 | 22.14 | 26.11 | 20.06
DCS880 | 20.01 | 20.13 | 22.11 | NA | 19.11 | 22.12 | 22.14 | 26.11 | 20.15
ACH580 | 20.01 | 31.11 | 22.11 | NA | 19.11 | 22.18 | See 19.11 | 26.11 | 20.06
ACQ580 | 20.01 | 31.11 | 22.11 | NA | 19.11 | 22.18 | See 19.11 | 26.11 | 20.06
| 20.01 | 31.11 | 22.11 | NA | 19.11 | 22.18 | See 19.11 | 26.11 | 20.06
| Ext1/2 Sel Setting | Spd Ref1/2 Sel (yes) | Spd Ref1/2 Sel (No) |  | FALSE
ACS380 | FBA A MCW bit 11 | "See Ext1/Ext2 Sel" | "See Ext1/Ext2 Sel"
ACS480 | FBA A MCW bit 11 | "See Ext1/Ext2 Sel" | "See Ext1/Ext2 Sel"
ACS580 | FBA A MCW bit 11 | "See Ext1/Ext2 Sel" | "See Ext1/Ext2 Sel"
ACS880 | FBA A MCW bit 11 | Other (Define bit) | Follow Ext1/Ext2 Sel
DCS880 | Other (6.01 bit11) | Other (Define bit) | Speed Reference 1
ACH580 | FBA A MCW bit 11 | "See Ext1/Ext2 Sel" | "See Ext1/Ext2 Sel"
ACQ580 | FBA A MCW bit 11 | "See Ext1/Ext2 Sel" | "See Ext1/Ext2 Sel"
4
ABB VFD
ABB All-Compatible VFD
ABB Drives Profile
Data - INT
Note on H3: If the drive being used is ACS880 or DCS880, then define the option slot which the Ethernet IP module is mounted. Otherwise, if drive being used is ACS380, ACS480, ACx580 then select "Enable" as Ethernet IP module can only be mounted in one location on the VFD and it must be turned on.
Note on H4: Once this parameter is set to Fault, the ABB Drive will enter into a faulted state until PLC comms are established, at that time the fault can be reset. Refer to the resprective ABB Drive Firmware Manual for a description of each setting available.
Note on H7: This configuraiton tool automatically defines the proper setting for this parameter based on other selections in the tool. Note: If Speed Reference 1 (parameter 22.11) is not being controlled via communications, then set cell B9=NO (Speed Reference 1 Control) to the left to represent this actual setup, which will then automatically configure this parameter. If 22.11= AI1 scaled for example, this parameter must be set to "Speed" to properly scale the speed feedback to the PLC.
Note on H8: This configuraiton tool automatically defines the proper setting for this parameter based on other selections in the tool. Note: If Torque Reference 1 (parameter 26.11) is not being controlled via communications, then set cell B11=NO (Torque Reference 1 Control) to the left to represent this actual setup, which will then automatically configure this parameter. If parameter 26.11= AI1 scaled for example, then this parameter must be set to "Torque" to properly scale Torque Feedback to the PLC if the profile utilized has torque included (This is taken into account by selecting "YES" in Step 3 of the "Profile Selection" tab.)
Note on H10: This parameter is read only, and should simply be checked to make sure "Ethernet" or "Ethernet/IP" is displayed which signifies that the FENA or FEIP module (respectively) is recognized by the VFD
Note on H11: This parameter configures the VFD for ABB Drives Profile, this setting is used in conjunction with the Rockwell EIP Module Config screen shown to the right to establish comms between PLC and the ABB VFD.
Note on D13: Parameter 31.11 is the Fault Reset Selection parameter.
Note on H17: The FENA user manual has a table description of different formats for the Subnet Mask and the associated CIDR setting. 24 = 255.255.255.0
Note on H18: First Octet address for utilizing comms via a gateway from another network
Note on H19: Second Octet address for utilizing comms via a gateway from another network
Note on H20: Third Octet address for utilizing comms via a gateway from another network
Note on H21: Forth Octet address for utilizing comms via a gateway from another network
Note on H22: The actual Timeout time is 100ms x Control Timeout Setting. This is the time in which the FENA or FEIP module will stop sending data to the ABB Drive to signal comm loss. Comm Loss Function (50.02) and Comm Loss timeout (50.03) define what the ABB Drive will do when it stops receiving comms from the Ethernet IP Module.
Note on H23: This parameter defines the action of the Ethernet module takes when a Network Idle State is determined. Off-line will halt comms with the drive, and the Drive Comm Loss function (parameter 50.02) determines the actioin the drive will take. Value of 1 means Online, so module will continue to transfer the last data to the VFD when Network is Idle
Note on H24: Parameter Refresh must be triggered after any changes are made to parameters in Group 50, 51, 52, 53 before they take effect and become active
Note on H31: This parameter should be set the same as the Maximum desired operation Speed or Frequency in the Reverse Rotation. Because ODVA Basic Profile does not support direction, this parameter can be set to 0 rpm or Hz.
Note on H32: This parameter should be set the same as the Maximum desired operation Speed or Frequency.
Note on H33: This parameter should be set the same as the Maximum desired operation Speed or Frequency.
Note on H34: This parameter adjusts power scaling. Default is 1000 which could be too high. Adjusting this parameter adjusts resolution of the powert feedback
Note on H35: This parameter adjusts current scaling. Default is 10000 which is likely too high. Adjusting this parameter adjusts resolution of the current feedback

## Transparent 16 Profile (hidden)
Ethernet IP Transparent 16 (Bit) Profile |  |  |  | FENA-11/21 Configuration Parameters (Group 50 & 51)
|  |  |  | Parameter Name | Parameter | Parameter Setting |  | Rockwell Logix 5000 Software Configuration to add ABB VFDs as a new Ethernet IP Device
VFD Signals Controlled by PLC over EIP |  |  |  | FBA A enable | 50.01 | Please Select.. |  | Note: The configuration below is specific to the Transparent 16 Profile and the data
Signal | No/Yes | Parameter | Parameter Setting | FBA A comm loss func | 50.02 | Fault Always |  | supplied on the "Profile Selection" Tab of this Spreadsheet Tool. This PLC configuration
EXT1/EXT2 Select | NO | 19.11 | EXT1 | FBA ref1 type | 50.04 | Auto |  | matches the parameters defined on this page and will deliver successful Communications
EXT1 Run Command | YES | 20.01 | Fieldbus A | FBA ref2 type | 50.05 | Auto |  | between the PLC and the ABB VFD via Ethernet IP
EXT2 Run Command | NO | 20.06 | "User Defines Setting" | FBA actual 1 type | 50.07 | Auto
Direction Command | YES | 20.21 | Request | FBA actual 2 type | 50.08 | Torque
Speed Reference 1 | YES | 22.11 | FB A ref1 | FBA A SW transparent source | 50.09 | User Status Word 1
Speed Reference 2 | NO | 22.18 | "User Defines Setting" | FBA A act1 transparent source | 50.1 | Not selected
Speed Ref 1/2 Sel | NO | See 19.11 | "See Ext1/Ext2 Sel" | FBA A act2 transparent source | 50.11 | Not selected
Torque Reference 1 | NO | 26.11 | "User Defines Setting"
Fault Reset | YES | 31.11 | FBA A MCW bit 7 | FBA A Type | 51.01 | Ethernet
|  |  |  | Protocol / Profile | 51.02 | 102 (EIP T16)
Parameters for Configuring User Defined Status Word |  |  |  | IP configuration | 51.04 | 0 (Static) | [7 empty] | NA | NA
Signal |  | Parameter | Parameter Setting | IP Address 1 | 51.05 | 192 | [7 empty] | NA | NA
User Status Word Bit 0 Sel |  | 6.6 | "User Selects Bit Source" | IP Address 2 | 51.06 | 168 | [7 empty] | 1 | 0
User Status Word Bit 1 Sel |  | 6.61 | "User Selects Bit Source" | IP Address 3 | 51.07 | 3 |  |  |  | 192 | 168 | 3 | 3
User Status Word Bit 2 Sel |  | 6.62 | "User Selects Bit Source" | IP Address 4 | 51.08 | 3
User Status Word Bit 3 Sel |  | 6.63 | "User Selects Bit Source" | Subnet CIDR | 51.09 | 24
User Status Word Bit 4 Sel |  | 6.64 | "User Selects Bit Source" | GW Address 1 | 51.1 | 0
User Status Word Bit 5 Sel |  | 6.65 | "User Selects Bit Source" | GW Address 2 | 51.11 | 0
User Status Word Bit 6 Sel |  | 6.66 | "User Selects Bit Source" | GW Address 3 | 51.12 | 0
User Status Word Bit 7 Sel |  | 6.67 | "User Selects Bit Source" | GW Address 4 | 51.13 | 0
User Status Word Bit 8 Sel |  | 6.68 | "User Selects Bit Source" | T16 Scale | 51.19 | 99
User Status Word Bit 9 Sel |  | 6.69 | "User Selects Bit Source" | Control Timeout | 51.2 | 20
User Status Word Bit 10 Sel |  | 6.7 | "User Selects Bit Source" | Idle Action | 51.21 | 0 (Off-line)
User Status Word Bit 11 Sel |  | 6.71 | "User Selects Bit Source" | FBA Par Refresh | 51.27 | Configure
User Status Word Bit 12 Sel |  | 6.72 | "User Selects Bit Source"
User Status Word Bit 13 Sel |  | 6.73 | "User Selects Bit Source"
User Status Word Bit 14 Sel |  | 6.74 | "User Selects Bit Source" | Other VFD Parameters that Accompany Communication Control
User Status Word Bit 15 Sel |  | 6.75 | "User Selects Bit Source" | Parameter Name | Parameter | Parameter Setting | Units
|  |  |  | Acceleration Time 1 | 23.12 | 5.00 s | s
Parameters for Configuring User Defined Data Words |  |  |  | Deceleration Time 1 | 23.13 | 5.00 s | s
Inputs (Read) to PLC from VFD |  | Outputs (Write) from PLC to VFD |  | Minimum Speed | 30.11 | 0 | rpm
Parameter | Parameter Setting | Parameter | Parameter Setting | Maximum Speed | 30.12 | 1800 | rpm
52.01 (16bit) | NA | 53.01 (16bit) | NA | Speed Scaling | 46.01 | 1800 | rpm
52.02 (16bit) | NA | 53.02 (16bit) | NA
52.03 (16bit) | NA | 53.03 (16bit) | NA
52.04 (16bit) | NA | 53.04 (16bit) | NA
52.05 (16bit) | NA | 53.05 (16bit) | NA
52.06 (16bit) | NA | 53.06 (16bit) | NA
52.07 (16bit) | NA | 53.07 (16bit) | NA
52.08 (16bit) | NA | 53.08 (16bit) | NA
52.09 (16bit) | NA | 53.09 (16bit) | NA
52.10 (16bit) | NA | 53.10 (16bit) | NA
[7 empty] | Output | Input | Size
[7 empty] | NA | NA | NA
Assembly Instances for ODVA ACDC Basic Profile
[7 empty] | Output | Input | Size
| NO | "User Defines Setting" |  |  |  |  | NA | NA | NA
| YES | "Define Bit in User CW 6.03" |  |  |  |  | 11 | 61 | 2
| NO | "User Defines Setting" |  |  |  |  | 12 | 62 | 3
| YES | "Define Bit in User CW 6.03" |  |  |  |  | 111 | 161 | 12
| NO | "User Defines Setting" |  |  |  |  | 112 | 162 | 13
| YES | FB A ref1
| NO | "User Defines Setting"
| YES | "Define Bit in User CW 6.03"
| NO | EXT1
| YES | "Define Bit in User CW 6.03"
| NO | "User Defines Setting"
| YES | FB A ref2
| NO | "User Defines Setting"
| YES | FB A ref2
4
ABB VFD
ABB ACS880 or DCS880
Transparent 16 Profile
Data - INT
Note on H3: If the drive being used is ACS880 or DCS880, then define the option slot which the Ethernet IP module is mounted. This will also activate the module and settings for Group 51 parameters will then be visible.
Note on H4: Once this parameter is set to Fault, the ABB Drive will enter into a faulted state until PLC comms are established, at that time the fault can be reset. A setting of Fault Always should be utilized with Transparent Profiles if Comm Loss Protection is desired. Refer to the respective ABB Drive Firmware Manual for a description of each setting available.
Note on H7: This configuraiton tool automatically defines the proper setting for this parameter based on other selections in the tool. Note: If Speed Reference 1 (parameter 22.11) is not being controlled via communications, then set cell B9=NO (Speed Reference 1 Control) to the left to represent this actual setup, which will then automatically configure this parameter. Also, for a further explanation of this parameter, see comment given in parameter 50.10 below.
Note on H8: This configuraiton tool automatically defines the proper setting for this parameter based on other selections in the tool. Note: If Torque Reference 1 (parameter 26.11) is not being controlled via communications, then set cell B11=NO (Torque Reference 1 Control) to the left to represent this actual setup, which will then automatically configure this parameter. Also, for a further explanation of this parameter, see comment given in parameter 50.11 below.
Note on H9: User Status Word 1 is parameter 6.50 (select 16bit format). The bits of this word are user defined by parameters 6.60-6.75 shown to the left
Note on H10: This parameter is only funtional for defining the first Actual Signal returned to the PLC when operating in Transparent mode if parameter 50.07 = Transparent. When 50.07 = Auto, the 1st Actual signal sent to the PLC will be based on the controlling reference defined for EXT1 control location, which is normally a speed reference. Thus if parameter 22.11= FBA A ref1, then the first actual signal sent to the PLC will be Actual Speed. However, if 22.11 = AI1 Scaled for example, it is necessary to set 50.07 = Speed to return the Actual Speed to the PLC with the scaling defined in the "Profile Selection" tab. Note: When 50.07 = Transparent, this parameter defines the 1st Actual signal sent to the PLC, the scaling on the signal will not match that which is defined in the IO table located in the "Profile Selection" tab.
Note on H11: This parameter is only funtional for defining the 2nd Actual Signal returned to the PLC when operating in Transparent mode if parameter 50.08 = Transparent. When 50.08 = Auto, the 2nd Actual signal sent to the PLC will be based on the controlling reference defined for EXT2 control location, which is normally a torque reference. Thus if parameter 26.11= FBA A ref2, then the 2nd actual signal sent to the PLC will be Actual Torque. However, if 26.11 = AI1 Scaled for example, it is necessary to set 50.08 = Torque to return the Actual Torque to the PLC with the scaling defined in the "Profile Selection" tab. Note: When 50.08 = Transparent, this parameter defines the 2nd Actual signal sent to the PLC, the scaling on the signal will not match that which is defined in the IO table located in the "Profile Selection" tab.
Note on D13: Parameter 31.11 is the Fault Reset Selection parameter.
Note on H13: This parameter is read only, and should simply be checked to make sure "Ethernet" or "Ethernet/IP" is displayed which signifies that the FENA or FEIP module (respectively) is recognized by the VFD
Note on H14: This parameter configures the VFD for Transparent 16 Profile, this setting is used in conjunction with the Rockwell EIP Module Config screen shown to the right to establish comms between PLC and the ABB VFD.
Note on D17: This parameter defines Bit 0 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on D18: This parameter defines Bit 1 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on D19: This parameter defines Bit 2 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on D20: This parameter defines Bit 3 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on H20: The FENA user manual has a table description of different formats for the Subnet Mask and the associated CIDR setting. 24 = 255.255.255.0
Note on D21: This parameter defines Bit 4 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on H21: First Octet address for utilizing comms via a gateway from another network
Note on D22: This parameter defines Bit 5 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on H22: Second Octet address for utilizing comms via a gateway from another network
Note on D23: This parameter defines Bit 6 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on H23: Third Octet address for utilizing comms via a gateway from another network
Note on D24: This parameter defines Bit 7 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on H24: Forth Octet address for utilizing comms via a gateway from another network
Note on D25: This parameter defines Bit 8 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on H25: The T16 (Transparent 16) Scale Factor of 99 equates out to a 1 = 1rpm scaling for Speed Reference and Actual Speed
Note on D26: This parameter defines Bit 9 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on H26: The actual Timeout time is 100ms x Control Timeout Setting. This is the time in which the FENA or FEIP module will stop sending data to the ABB Drive to signal comm loss. Comm Loss Function (50.02) and Comm Loss timeout (50.03) define what the ABB Drive will do when it stops receiving comms from the Ethernet IP Module.
Note on D27: This parameter defines Bit 10 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on H27: This parameter defines the action of the Ethernet module takes when a Network Idle State is determined. Off-line will halt comms with the drive, and the Drive Comm Loss function (parameter 50.02) determines the actioin the drive will take. Value of 1 means Online, so module will continue to transfer the last data to the VFD when Network is Idle
Note on D28: This parameter defines Bit 11 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on H28: Parameter Refresh must be triggered after any changes are made to parameters in Group 50, 51, 52, 53 before they take effect and become active
Note on D29: This parameter defines Bit 12 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on D30: This parameter defines Bit 13 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on D31: This parameter defines Bit 14 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on D32: This parameter defines Bit 15 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on H35: This parameter should be set the same as the Maximum desired operation Speed or Frequency in the Reverse Rotation. Because ODVA Basic Profile does not support direction, this parameter can be set to 0 rpm or Hz.
Note on H36: This parameter should be set the same as the Maximum desired operation Speed or Frequency.
Note on H37: This parameter should be set the same as the Maximum desired operation Speed or Frequency.

## Transparent 32 Profile (hidden)
Ethernet IP Transparent 32 (Bit) Profile |  |  |  | FENA-11/21 Configuration Parameters (Group 50 & 51)
|  |  |  | Parameter Name | Parameter | Parameter Setting |  | Rockwell Logix 5000 Software Configuration to add ABB VFDs as a new Ethernet IP Device
VFD Signals Controlled by PLC over EIP |  |  |  | FBA A enable | 50.01 | Please Select.. |  | Note: The configuration below is specific to the Transparent 32 Profile and the data
Signal | No/Yes | Parameter | Parameter Setting | FBA A comm loss func | 50.02 | Fault Always |  | supplied on the "Profile Selection" Tab of this Spreadsheet Tool. This PLC configuration
EXT1/EXT2 Select | NO | 19.11 | EXT1 | FBA ref1 type | 50.04 | Auto |  | matches the parameters defined on this page and will deliver successful Communications
EXT1 Run Command | YES | 20.01 | Fieldbus A | FBA ref2 type | 50.05 | Auto |  | between the PLC and the ABB VFD via Ethernet IP
EXT2 Run Command | NO | 20.06 | "User Defines Setting" | FBA actual 1 type | 50.07 | Auto
Direction Command | YES | 20.21 | Request | FBA actual 2 type | 50.08 | Torque
Speed Reference 1 | YES | 22.11 | FB A ref1 | FBA A SW transparent source | 50.09 | User Status Word 1
Speed Reference 2 | NO | 22.18 | "User Defines Setting" | FBA A act1 transparent source | 50.1 | Not selected
Speed Ref 1/2 Sel | NO | See 19.11 | "See Ext1/Ext2 Sel" | FBA A act2 transparent source | 50.11 | Not selected
Torque Reference 1 | NO | 26.11 | "User Defines Setting"
Fault Reset | YES | 31.11 | FBA A MCW bit 7 | FBA A Type | 51.01 | Ethernet
|  |  |  | Protocol / Profile | 51.02 | 103 (EIP T32)
Parameters for Configuring User Defined Status Word |  |  |  | IP configuration | 51.04 | 0 (Static) | [7 empty] | NA | NA
Signal |  | Parameter | Parameter Setting | IP Address 1 | 51.05 | 192 | [7 empty] | NA | NA
User Status Word Bit 0 Sel |  | 6.6 | "User Selects Bit Source" | IP Address 2 | 51.06 | 168 | [7 empty] | 1 | 0
User Status Word Bit 1 Sel |  | 6.61 | "User Selects Bit Source" | IP Address 3 | 51.07 | 3 |  |  |  | 192 | 168 | 3 | 3
User Status Word Bit 2 Sel |  | 6.62 | "User Selects Bit Source" | IP Address 4 | 51.08 | 3
User Status Word Bit 3 Sel |  | 6.63 | "User Selects Bit Source" | Subnet CIDR | 51.09 | 24
User Status Word Bit 4 Sel |  | 6.64 | "User Selects Bit Source" | GW Address 1 | 51.1 | 0
User Status Word Bit 5 Sel |  | 6.65 | "User Selects Bit Source" | GW Address 2 | 51.11 | 0
User Status Word Bit 6 Sel |  | 6.66 | "User Selects Bit Source" | GW Address 3 | 51.12 | 0
User Status Word Bit 7 Sel |  | 6.67 | "User Selects Bit Source" | GW Address 4 | 51.13 | 0
User Status Word Bit 8 Sel |  | 6.68 | "User Selects Bit Source" | T16 Scale | 51.19 | 99
User Status Word Bit 9 Sel |  | 6.69 | "User Selects Bit Source" | Control Timeout | 51.2 | 20
User Status Word Bit 10 Sel |  | 6.7 | "User Selects Bit Source" | Idle Action | 51.21 | 0 (Off-line)
User Status Word Bit 11 Sel |  | 6.71 | "User Selects Bit Source" | FBA Par Refresh | 51.27 | Configure
User Status Word Bit 12 Sel |  | 6.72 | "User Selects Bit Source"
User Status Word Bit 13 Sel |  | 6.73 | "User Selects Bit Source"
User Status Word Bit 14 Sel |  | 6.74 | "User Selects Bit Source" | Other VFD Parameters that Accompany Communication Control
User Status Word Bit 15 Sel |  | 6.75 | "User Selects Bit Source" | Parameter Name | Parameter | Parameter Setting | Units
|  |  |  | Acceleration Time 1 | 23.12 | 5.00 s | s
Parameters for Configuring User Defined Data Words |  |  |  | Deceleration Time 1 | 23.13 | 5.00 s | s
Inputs (Read) to PLC from VFD |  | Outputs (Write) from PLC to VFD |  | Minimum Speed | 30.11 | 0 | rpm
Parameter | Parameter Setting | Parameter | Parameter Setting | Maximum Speed | 30.12 | 1800 | rpm
52.01 (32bit) | NA | 53.01 (32bit) | NA | Speed Scaling | 46.01 | 1800 | rpm
52.02 | NA | 53.02 | NA
52.03 (32bit) | NA | 53.03 (32bit) | NA
52.04 | NA | 53.04 | NA
52.05 (32bit) | NA | 53.05 (32bit) | NA
52.06 | NA | 53.06 | NA
52.07 (32bit) | NA | 53.07 (32bit) | NA
52.08 | NA | 53.08 | NA
52.09 (32bit) | NA | 53.09 (32bit) | NA
52.1 | NA | 53.1 | NA
[7 empty] | Output | Input | Size16 | Size32
| NO | "User Defines Setting" |  |  |  |  | NA | NA | NA | NA
| YES | "Define Bit in User CW 6.03"
| NO | "User Defines Setting"
| YES | "Define Bit in User CW 6.03"
| NO | "User Defines Setting"
| YES | FB A ref1 |  |  |  |  | Assembly Instances for ODVA ACDC Basic Profile
| NO | "User Defines Setting" |  |  |  |  | Output | Input | 16bit | 32bit
| YES | "Define Bit in User CW 6.03" |  |  |  |  | NA | NA | NA | NA
| NO | EXT1 |  |  |  |  | 21 | 71 | 4 | 2
| YES | "Define Bit in User CW 6.03" |  |  |  |  | 22 | 72 | 6 | 3
| NO | "User Defines Setting" |  |  |  |  | 121 | 171 | 14 | 7
| YES | FB A ref2 |  |  |  |  | 122 | 172 | 16 | 8
| NO | "User Defines Setting"
| YES | FB A ref2
4
ABB VFD
ABB ACS880 or DCS880
Transparent 32 Profile
Data - DINT
32bit PLC Data Format Configuration along with the ABB ACS880/DCS880 Configured for Transparent 32 Profile is shown above. Note: Control Word, Status Word, Reference1, Reference2, Actual1, Actual2 are all 32 bit word format by default, all other User Defined Data formats must be manually defined as 32 Bit Format by the user when configuring the parameters in Groups 52 and 53 from the ACS880/DCS880 keypad. Note: If the VFD User Defined data words are configured for 16bit format, then a maximum total of 13 words of data can be communicated but two user defined data words will appear per 32bit PLC register. If this type of configuration is needed, please contact your local ABB Application Engineer for assistance. If the VFD User Defined Data Words are configured for 32bit format, then a max of 8 words of data will be communicated. With both PLC and VFD data formats being 32bit format, one communicated Data word will appear per 32bit PLC register.
Group 52 and 53 User Defined Data Parameters shown to the left reference being configured as 32bit format. Notice that every other parameter is used because each data pointer register is only 16bit, thus two registers are needed when communicating 32bit formatted words.
Important!
Note on H3: If the drive being used is ACS880 or DCS880, then define the option slot which the Ethernet IP module is mounted. This will also activate the module and settings for Group 51 parameters will then be visible.
Note on H4: Once this parameter is set to Fault, the ABB Drive will enter into a faulted state until PLC comms are established, at that time the fault can be reset. A setting of Fault Always should be utilized with Transparent Profiles if Comm Loss Protection is desired. Refer to the respective ABB Drive Firmware Manual for a description of each setting available.
Note on H7: This configuraiton tool automatically defines the proper setting for this parameter based on other selections in the tool. Note: If Speed Reference 1 (parameter 22.11) is not being controlled via communications, then set cell B9=NO (Speed Reference 1 Control) to the left to represent this actual setup, which will then automatically configure this parameter. Also, for a further explanation of this parameter, see comment given in parameter 50.10 below.
Note on H8: This configuraiton tool automatically defines the proper setting for this parameter based on other selections in the tool. Note: If Torque Reference 1 (parameter 26.11) is not being controlled via communications, then set cell B11=NO (Torque Reference 1 Control) to the left to represent this actual setup, which will then automatically configure this parameter. Also, for a further explanation of this parameter, see comment given in parameter 50.11 below.
Note on H9: User Status Word 1 is parameter 6.50. The bits of this word are user defined by parameters 6.60-6.75 shown to the left
Note on H10: This parameter is only funtional for defining the first Actual Signal returned to the PLC when operating in Transparent mode if parameter 50.07 = Transparent. When 50.07 = Auto, the 1st Actual signal sent to the PLC will be based on the controlling reference defined for EXT1 control location, which is normally a speed reference. Thus if parameter 22.11= FBA A ref1, then the first actual signal sent to the PLC will be Actual Speed. However, if 22.11 = AI1 Scaled for example, it is necessary to set 50.07 = Speed to return the Actual Speed to the PLC with the scaling defined in the "Profile Selection" tab. Note: When 50.07 = Transparent, and this parameter defines the 1st Actual signal sent to the PLC, the scaling on the signal will not match that which is defined in the IO table located in the "Profile Selection" tab, rather the scaling will be the native scaling defined for 32bit communications found in the Firmware Manual
Note on H11: This parameter is only funtional for defining the 2nd Actual Signal returned to the PLC when operating in Transparent mode if parameter 50.08 = Transparent. When 50.08 = Auto, the 2nd Actual signal sent to the PLC will be based on the controlling reference defined for EXT2 control location, which is normally a torque reference. Thus if parameter 26.11= FBA A ref2, then the 2nd actual signal sent to the PLC will be Actual Torque. However, if 26.11 = AI1 Scaled for example, it is necessary to set 50.08 = Torque to return the Actual Torque to the PLC with the scaling defined in the "Profile Selection" tab. Note: When 50.08 = Transparent, and this parameter defines the 2nd Actual signal sent to the PLC, the scaling on the signal will not match that which is defined in the IO table located in the "Profile Selection" tab, rather the scaling will be the native scaling defined for 32bit communications found in the Firmware Manual
Note on D13: Parameter 31.11 is the Fault Reset Selection parameter.
Note on H13: This parameter is read only, and should simply be checked to make sure "Ethernet" or "Ethernet/IP" is displayed which signifies that the FENA or FEIP module (respectively) is recognized by the VFD
Note on H14: This parameter configures the VFD for Transparent 32 Profile, this setting is used in conjunction with the Rockwell EIP Module Config screen shown to the right to establish comms between PLC and the ABB VFD.
Note on D17: This parameter defines Bit 0 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on D18: This parameter defines Bit 1 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on D19: This parameter defines Bit 2 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on D20: This parameter defines Bit 3 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on H20: The FENA user manual has a table description of different formats for the Subnet Mask and the associated CIDR setting. 24 = 255.255.255.0
Note on D21: This parameter defines Bit 4 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on H21: First Octet address for utilizing comms via a gateway from another network
Note on D22: This parameter defines Bit 5 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on H22: Second Octet address for utilizing comms via a gateway from another network
Note on D23: This parameter defines Bit 6 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on H23: Third Octet address for utilizing comms via a gateway from another network
Note on D24: This parameter defines Bit 7 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on H24: Forth Octet address for utilizing comms via a gateway from another network
Note on D25: This parameter defines Bit 8 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on H25: The T16 (Transparent 16) Scale Factor of 99 equates out to a 1 = 1rpm scaling for Speed Reference and Actual Speed
Note on D26: This parameter defines Bit 9 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on H26: The actual Timeout time is 100ms x Control Timeout Setting. This is the time in which the FENA or FEIP module will stop sending data to the ABB Drive to signal comm loss. Comm Loss Function (50.02) and Comm Loss timeout (50.03) define what the ABB Drive will do when it stops receiving comms from the Ethernet IP Module.
Note on D27: This parameter defines Bit 10 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on H27: This parameter defines the action of the Ethernet module takes when a Network Idle State is determined. Off-line will halt comms with the drive, and the Drive Comm Loss function (parameter 50.02) determines the actioin the drive will take. Value of 1 means Online, so module will continue to transfer the last data to the VFD when Network is Idle
Note on D28: This parameter defines Bit 11 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on H28: Parameter Refresh must be triggered after any changes are made to parameters in Group 50, 51, 52, 53 before they take effect and become active
Note on D29: This parameter defines Bit 12 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on D30: This parameter defines Bit 13 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on D31: This parameter defines Bit 14 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on D32: This parameter defines Bit 15 of the User Defined Status word located in parameter 6.50. This allows the user to define the Status Word Bit Structure to align with existing PLC programming, or a desired Structure with Bits that may be different from the Normal ABB Drive Status Word
Note on H35: This parameter should be set the same as the Maximum desired operation Speed or Frequency in the Reverse Rotation. Because ODVA Basic Profile does not support direction, this parameter can be set to 0 rpm or Hz.
Note on H36: This parameter should be set the same as the Maximum desired operation Speed or Frequency.
Note on H37: This parameter should be set the same as the Maximum desired operation Speed or Frequency.

## Profile and Instances (hidden)
ACDC Profiles
EIP ACDC Profile - also referred to as ODVA Profiles, is a control profile that is specified by a third party organization (Open Devicenet Vendors Association) that was defined so that all manufacturers AC and DC drives would look and control the same if this profile was adhered to. There are benefits to utilizing this type of profile, as it is very simplistic and thus makes writing the PLC control logic very fast and simple to maintain. The other benefit is that the speed reference and actual speed feedback are also simplified as the scaling is 1=1rpm. There are two versions of the ACDC ODVA Profile, "Basic" and "Extended". The "Basic" version of the ODVA Control profile does not support change of motor direction commands where the Extended ACDC does support it. The Extended ACDC Profile also supports more status bits such as: VFD Warning Status, Direction of operation, VFD Ready Status, and motor At Speed status. The ACDC Profiles support Torque Reference and Actual Torque feedback, but it should be known that the scaling is 1=1Nm, and may not provide the resolution required by the application, and would require some math functionality in the PLC if Torque was normally looked at in % of Motor Nominal or in lbft. Note: If Torque control is not required, but torque feedback is desired, you can utilize one of the available Input Data Pointers to represent motor torque to provide the level of resolution or different unit of measure.
ABB Profile
ABB Drives Profile - Is a control profile that was designed with larger process or coordinated system control in mind. This profile supports much more control functionality than the ACDC Profiles, such as switching between two control locations, jogging, multiple ways of stopping the VFD (Coast, Ramp, Torque Limit), and profides bits for manipulation of the speed reference ramp generator. However, because of this additional functionality, it should be known from the PLC programmers perspective that there is a State Machine flow to the control logic that must be satisfied to issue run commands to the VFD. The speed reference provides a higher level of resolution than that of the ACDC Profile, but would also require math to convert +/-20000 to rpm or hz based on the control mode of the VFD. ABB Drives Profile also supports Torque Reference and Actual Torque Feedback. Torque has a higher level of resolution for more finite control vs the ACDC Profile if application requires torque control of the motor.
Transparent Profiles
Transparent Profiles - Two different Transparent profiles are supported only by the ACS880 at present time, they are: Transparent 16 and Transparent 32. The Transparent Profiles can be utilized to allow the PLC programmer to customize the VFD control and status bit structure to their liking. It is possible to reuse another VFD manufacturers Control and Status word control bit structures for the ABB ACS880, thus mimicking the other VFD by configuring the ACS880 to utilize a custom bit structure. Just realize, that by utilizing the Transparent Profiles it will require more parameters to be configured in the ACS880 which will define the bit structure of the Control Word and the Status Word. It should also be known that by selecting Transparent 32, the user is reducing the number of total data words transferred across Ethernet IP (ie Transparent 16 supports a max data packet of 13 words, Transparent 32 only supports a maximum size of 8) Both Transparent Profiles support Speed Control and Torque Control if required. The scaling utilized can be manipulated by the parameters found in 50.04-50.08 and the feedback signals can be user defined by parameters 50.09-50.11 along with the Input and Output Data Pointers in groups 52 and 53.